## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 66 | 67 | 126 | 4 | 49.8 | 19.73 | 50 | 82.2 | 17.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 67 | 64 | 126 | 4 | 49.8 | 17.49 | 50 | 82.2 | 17.2 | 61.6 | 39.5 | 203.9 | 206.3 | 203.9 | NO
| NG | 64 | 65 | 126 | 4 | 49.8 | 17.49 | 50 | 82.2 | 17.2 | 61.6 | 39.5 | 203.9 | 206.3 | 203.9 | NO
| NG | 65 | 119 | 126 | 4 | 49.8 | 17.49 | 50 | 82.2 | 17.2 | 61.6 | 39.5 | 203.9 | 206.3 | 203.9 | NO
| NG | 119 | 41 | 126 | 4 | 49.8 | 14.75 | 50 | 82.2 | 17.2 | 64.7 | 35.8 | 203.9 | 210.7 | 203.9 | NO
| NG | 41 | 40 | 126 | 4 | 49.8 | 14.75 | 50 | 82.2 | 17.2 | 64.7 | 35.8 | 203.9 | 210.7 | 203.9 | NO
| NG | 40 | 39 | 126 | 4 | 49.8 | 14.75 | 50 | 82.2 | 17.2 | 64.7 | 35.8 | 203.9 | 210.7 | 203.9 | NO
| NG | 39 | 38 | 126 | 4 | 49.8 | 12.9 | 50 | 82.2 | 17.2 | 66.9 | 31.4 | 203.9 | 214.7 | 203.9 | NO
| NG | 38 | 37 | 126 | 4 | 49.8 | 12.62 | 50 | 82.2 | 17.2 | 67.2 | 30.7 | 203.9 | 215.4 | 203.9 | NO
| NG | 37 | 33 | 126 | 4 | 49.8 | 12.62 | 50 | 82.2 | 17.2 | 67.2 | 30.7 | 203.9 | 215.4 | 203.9 | NO
| NG | 33 | 32 | 126 | 4 | 49.8 | 10.5 | 50 | 82.2 | 17.2 | 69.7 | 30.7 | 203.9 | 215.4 | 203.9 | NO
| NG | 32 | 31 | 126 | 4 | 49.8 | 10.5 | 50 | 82.2 | 17.2 | 69.7 | 30.7 | 203.9 | 215.4 | 203.9 | NO
| NG | 31 | 3 | 126 | 4 | 49.8 | 10.25 | 50 | 82.2 | 17.2 | 69.9 | 30.7 | 203.9 | 215.4 | 203.9 | NO
| NG | 3 | 2 | 126 | 4 | 49.8 | 9.69 | 50 | 82.2 | 17.2 | 69.9 | 30.7 | 203.9 | 215.4 | 203.9 | NO
| NG | 105 | 79 | 97 | 8 | 31 | 29.86 | 50 | 82.2 | 17.2 | 45.4 | 60.8 | 215.2 | 203.9 | 203.9 | NO
| NG | 2 | 91 | 126 | 4 | 49.8 | 9.69 | 50 | 82.2 | 17.2 | 70.6 | 30.7 | 203.9 | 215.4 | 203.9 | NO
| NG | 79 | 48 | 97 | 8 | 31 | 29.51 | 50 | 82.2 | 17.2 | 45.8 | 60.8 | 215.1 | 203.9 | 203.9 | NO
| NG | 91 | 43 | 111 | 2 | 72.7 | 8.01 | 50 | 82.2 | 17.2 | 72.6 | 28.8 | 203.9 | 220.8 | 203.9 | NO
| NG | 48 | 103 | 97 | 8 | 31 | 16.15 | 50 | 82.2 | 17.2 | 61.9 | 56.7 | 213.1 | 206.4 | 206.4 | NO
| NG | 43 | 99 | 111 | 2 | 72.7 | 7.29 | 50 | 82.2 | 17.2 | 73.4 | 27 | 203.9 | 222.2 | 203.9 | NO
| NG | 103 | 80 | 97 | 8 | 31 | 16.15 | 50 | 82.2 | 17.2 | 61.9 | 56.7 | 213.1 | 206.4 | 206.4 | NO
| NG | 99 | 98 | 111 | 2 | 72.7 | 6.68 | 50 | 82.2 | 17.2 | 74.1 | 27 | 203.9 | 222.2 | 203.9 | NO
| NG | 80 | 81 | 97 | 8 | 31 | 16.15 | 50 | 82.2 | 17.2 | 61.9 | 56.7 | 213.1 | 206.4 | 206.4 | NO
| NG | 98 | 29 | 111 | 2 | 72.7 | 6.37 | 50 | 82.2 | 17.2 | 74.3 | 27 | 203.9 | 222.2 | 203.9 | NO
| NG | 81 | 82 | 97 | 8 | 31 | 15.84 | 50 | 82.2 | 17.2 | 62.3 | 55.9 | 213.1 | 206.9 | 206.9 | NO
| NG | 29 | 28 | 111 | 2 | 72.7 | 6.17 | 50 | 82.2 | 17.2 | 74.7 | 27 | 203.9 | 222.2 | 203.9 | NO
| NG | 82 | 83 | 97 | 8 | 31 | 15.84 | 50 | 82.2 | 17.2 | 62.3 | 55.3 | 213.1 | 207.3 | 207.3 | NO
1 | ** OPTIMAL ** | 83 | 10 | 85 | 4 | 62.4 | 5.07 | 50 | 82.2 | 17.2 | 66.2 | 29.1 | 213.3 | 221.7 | 213.3 | YES
| NG | 83 | 50 | 97 | 8 | 31 | 2.77 | 50 | 82.2 | 17.2 | 78.4 | 23.6 | 208.7 | 226.6 | 208.7 | NO
2 | OK | 10 | 11 | 85 | 4 | 62.4 | 4.84 | 50 | 82.2 | 17.2 | 75.7 | 28.5 | 212.5 | 222.1 | 212.5 | YES
3 | OK | 11 | 120 | 85 | 4 | 62.4 | 4.84 | 50 | 82.2 | 17.2 | 75.7 | 28.5 | 212.5 | 222.1 | 212.5 | YES
4 | OK | 120 | 84 | 85 | 4 | 62.4 | 4.84 | 50 | 82.2 | 17.2 | 75.7 | 20.8 | 212.5 | 227.4 | 212.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 37-006706
TR_B (available) | 55-016216
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 82.2
TR_B Baseline Loading% | 17.2
Total Scenarios Evaluated | 32
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 83
Switch Child Node | 10
Tie Node (TR_A side) | 85
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 62.4
Load Transferred (kW) | 5.07
TR_A Loading After (%) | 66.2
TR_B Loading After (%) | 29.1
Minimum Voltage (V) | 213.3