## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 74 | 106 | 123 | 9 | 72 | 6.71 | 50 | 82.2 | 22.8 | 74.4 | 38.5 | 203.5 | 217.3 | 203.5 | NO
| NG | 106 | 107 | 123 | 9 | 72 | 5.76 | 50 | 82.2 | 22.8 | 75.4 | 36.3 | 203.6 | 218.8 | 203.6 | NO
| NG | 107 | 75 | 123 | 9 | 72 | 5.57 | 50 | 82.2 | 22.8 | [5 empty] | NO | TR_A sim: loading 2956% (degenerate)
| NG | 75 | 76 | 123 | 9 | 72 | 5.07 | 50 | 82.2 | 22.8 | 76.2 | 34.6 | 203.6 | 219.7 | 203.6 | NO
| NG | 48 | 8 | 118 | 20 | 31.8 | 13.36 | 50 | 82.2 | 22.8 | 66.2 | 64.5 | 203.7 | 5.4 | 5.4 | NO
1 | ** OPTIMAL ** | 48 | 103 | 103 | 21 | 94.1 | 16.15 | 50 | 82.2 | 22.8 | 61.9 | 22.8 | 213.1 | 222.3 | 213.1 | YES
| NG | 76 | 77 | 123 | 9 | 72 | 4.1 | 50 | 82.2 | 22.8 | 77.4 | 32.3 | 203.7 | 220.2 | 203.7 | NO
| NG | 8 | 9 | 118 | 20 | 31.8 | 10.75 | 50 | 82.2 | 22.8 | 69.5 | 49.6 | 201.7 | 184.1 | 184.1 | NO
2 | OK | 103 | 80 | 80 | 21 | 127 | 16.15 | 50 | 82.2 | 22.8 | 61.9 | 22.8 | 213.1 | 222.3 | 213.1 | YES
| NG | 77 | 78 | 123 | 9 | 72 | 3.44 | 50 | 82.2 | 22.8 | 78.1 | 30.8 | 203.7 | 220.6 | 203.7 | NO
| NG | 9 | 54 | 118 | 20 | 31.8 | 9.04 | 50 | 82.2 | 22.8 | 71.6 | 47.5 | 201.8 | 187.4 | 187.4 | NO
| NG | 54 | 55 | 118 | 20 | 31.8 | 6.28 | 50 | 82.2 | 22.8 | 74.7 | 39 | 202.4 | 200.4 | 200.4 | NO
| NG | 55 | 117 | 118 | 20 | 31.8 | 2.56 | 50 | 82.2 | 22.8 | 79.1 | 29 | 203.3 | 214.9 | 203.3 | NO
| NG | 117 | 56 | 118 | 20 | 31.8 | 2.54 | 50 | 82.2 | 22.8 | 79.1 | 29 | 203.3 | 214.9 | 203.3 | NO
| NG | 56 | 7 | 118 | 20 | 31.8 | 2.53 | 50 | 82.2 | 22.8 | 79.1 | 29 | 203.3 | 215 | 203.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 37-006706
TR_B (available) | 67-037316
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 82.2
TR_B Baseline Loading% | 22.8
Total Scenarios Evaluated | 15
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 48
Switch Child Node | 103
Tie Node (TR_A side) | 103
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 94.1
Load Transferred (kW) | 16.15
TR_A Loading After (%) | 61.9
TR_B Loading After (%) | 22.8
Minimum Voltage (V) | 213.1