## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 1 | 3 | 141 | 7.85 | 50 | 71.8 | 61.5 | 66.2 | 80.7 | 185.7 | 210.1 | 185.7 | NO
| NG | 1 | 6 | 6 | 3 | 144.7 | 7.69 | 50 | 71.8 | 61.5 | 66.4 | 79.1 | 185.7 | 210.3 | 185.7 | NO
1 | ** OPTIMAL ** | 2 | 16 | 16 | 13 | 56.9 | 0.69 | 50 | 71.8 | 61.5 | 0 | 63.1 | 593942.1 | 213.3 | 213.3 | YES
| NG | 3 | 101 | 100 | 14 | 46.8 | 3.27 | 50 | 71.8 | 61.5 | 69.4 | 69.1 | 185.3 | 213.5 | 185.3 | NO
| NG | 3 | 137 | 137 | 15 | 79.6 | 0.86 | 50 | 71.8 | 61.5 | 71 | 63.5 | 187.1 | 213 | 187.1 | NO
| NG | 16 | 17 | 17 | 13 | 137.2 | 0.35 | 50 | 71.8 | 61.5 | 71.5 | 62.3 | 185.9 | 213.2 | 185.9 | NO
| NG | 34 | 79 | 79 | 8 | 94.4 | 7.5 | 50 | 71.8 | 61.5 | 64.9 | 79.2 | 202.9 | 209.6 | 202.9 | NO
| NG | 101 | 99 | 100 | 14 | 46.8 | 1.81 | 50 | 71.8 | 61.5 | 70.5 | 65.7 | 184.8 | 213.7 | 184.8 | NO
| NG | 137 | 78 | 78 | 15 | 120.4 | 0.26 | 50 | 71.8 | 61.5 | 71.5 | 62.1 | 186 | 213.4 | 186 | NO
| NG | 79 | 80 | 80 | 8 | 135.1 | 6.66 | 50 | 71.8 | 61.5 | 65.6 | 77.2 | 201.1 | 210 | 201.1 | NO
| NG | 99 | 100 | 100 | 14 | 46.8 | 0.08 | 50 | 71.8 | 61.5 | 71.7 | 61.7 | 185.5 | 213.6 | 185.5 | NO
| NG | 100 | 98 | 98 | 14 | 47.2 | 0.04 | 50 | 71.8 | 61.5 | 71.7 | 61.6 | 185.5 | 213.6 | 185.5 | NO
| NG | 82 | 83 | 14 | 23 | 39.6 | 8.15 | 50 | 71.8 | 61.5 | 64.4 | 81.4 | 206.6 | 206.9 | 206.6 | NO
| NG | 83 | 36 | 14 | 23 | 39.6 | 7.76 | 50 | 71.8 | 61.5 | 64.7 | 80.5 | 206.6 | 206.9 | 206.6 | NO
| NG | 36 | 14 | 14 | 23 | 39.6 | 6.18 | 50 | 71.8 | 61.5 | 66 | 76.4 | 203.3 | 210.5 | 203.3 | NO
| NG | 36 | 84 | 84 | 22 | 95.3 | 1.58 | 50 | 71.8 | 61.5 | 70.2 | 65.2 | 191.4 | 212.8 | 191.4 | NO
| NG | 14 | 15 | 15 | 24 | 39.9 | 5.06 | 50 | 71.8 | 61.5 | 66.9 | 73.9 | 203.9 | 210.1 | 203.9 | NO
| NG | 15 | 85 | 37 | 30 | 40.1 | 5.03 | 50 | 71.8 | 61.5 | 66.9 | 73.8 | 203.8 | 209.7 | 203.8 | NO
| NG | 85 | 37 | 37 | 30 | 40.1 | 5.03 | 50 | 71.8 | 61.5 | 66.9 | 73.8 | 203.8 | 209.7 | 203.8 | NO
| NG | 37 | 38 | 38 | 30 | 88.5 | 0.39 | 50 | 71.8 | 61.5 | 71.4 | 62.4 | 187.2 | 213.4 | 187.2 | NO
| NG | 37 | 39 | 127 | 17 | 41.8 | 4.64 | 50 | 71.8 | 61.5 | 67.2 | 73 | 203 | 208 | 203 | NO
| NG | 38 | 102 | 102 | 30 | 125.8 | 0.17 | 50 | 71.8 | 61.5 | 71.6 | 61.9 | 186.2 | 213.5 | 186.2 | NO
| NG | 39 | 127 | 127 | 17 | 41.8 | 0.2 | 50 | 71.8 | 61.5 | 71.6 | 62 | 186.4 | 213.5 | 186.4 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 37-014149
TR_B (available) | 24-005378
TR_A Rated kVA | 160
TR_B Rated kVA | 50
TR_A Baseline Loading% | 71.8
TR_B Baseline Loading% | 61.5
Total Scenarios Evaluated | 23
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 16
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 56.9
Load Transferred (kW) | 0.69
TR_A Loading After (%) | 0
TR_B Loading After (%) | 63.1
Minimum Voltage (V) | 213.3