## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 36 | 35 | 53 | 11 | 81.2 | 33.43 | 50 | 78.6 | 39.1 | 53.7 | 77.4 | 221.7 | 147 | 147 | NO
| NG | 36 | 41 | 0 | 0 | 57.1 | 34.28 | 50 | 78.6 | 39.1 | 53.7 | 82.6 | 209.2 | 199.6 | 199.6 | NO
| NG | 36 | 38 | 27 | 27 | 87.6 | 22.42 | 50 | 78.6 | 39.1 | 62.4 | 49.4 | 208.6 | 207.8 | 207.8 | NO
| NG | 36 | 94 | 30 | 27 | 148.1 | 17.5 | 50 | 78.6 | 39.1 | 65.9 | 61 | 207.9 | 197.1 | 197.1 | NO
| NG | 35 | 99 | 53 | 11 | 81.2 | 33.43 | 50 | 78.6 | 39.1 | 53.7 | 77.4 | 221.7 | 147 | 147 | NO
| NG | 41 | 14 | 0 | 0 | 57.1 | 28.62 | 50 | 78.6 | 39.1 | 57.8 | 74.7 | 208.9 | 205.9 | 205.9 | NO
| NG | 38 | 37 | 27 | 27 | 87.6 | 20.82 | 50 | 78.6 | 39.1 | 63.5 | 49.4 | 208.6 | 207.8 | 207.8 | NO
| NG | 94 | 93 | 30 | 27 | 148.1 | 17.42 | 50 | 78.6 | 39.1 | 66 | 60.9 | 207.9 | 197 | 197 | NO
| NG | 99 | 64 | 53 | 11 | 81.2 | 33.43 | 50 | 78.6 | 39.1 | 53.7 | 77.4 | 221.7 | 147 | 147 | NO
| NG | 14 | 13 | 0 | 0 | 57.1 | 25.46 | 50 | 78.6 | 39.1 | 60 | 70.4 | 208.7 | 204.9 | 204.9 | NO
| NG | 37 | 118 | 27 | 27 | 87.6 | 20.82 | 50 | 78.6 | 39.1 | 63.5 | 49.4 | 208.6 | 207.8 | 207.8 | NO
| NG | 93 | 105 | 30 | 27 | 148.1 | 6.55 | 50 | 78.6 | 39.1 | 73.8 | 46.8 | 207.8 | 219.9 | 207.8 | NO
| NG | 64 | 39 | 53 | 11 | 81.2 | 33.28 | 50 | 78.6 | 39.1 | 53.8 | 77.3 | 221.7 | 147.4 | 147.4 | NO
| NG | 13 | 10 | 0 | 0 | 57.1 | 24.17 | 50 | 78.6 | 39.1 | 60.9 | 68.7 | 208.7 | 209.7 | 208.7 | NO
| NG | 118 | 114 | 27 | 27 | 87.6 | 20.3 | 50 | 78.6 | 39.1 | 63.9 | 49.4 | 208.6 | 207.8 | 207.8 | NO
| NG | 105 | 101 | 30 | 27 | 148.1 | 5.96 | 50 | 78.6 | 39.1 | 74.3 | 46.1 | 207.7 | 219.8 | 207.7 | NO
| NG | 39 | 40 | 53 | 11 | 81.2 | 33.25 | 50 | 78.6 | 39.1 | 53.8 | 77.3 | 221.7 | 147.4 | 147.4 | NO
| NG | 10 | 11 | 0 | 0 | 57.1 | 22.97 | 50 | 78.6 | 39.1 | 61.8 | 67.1 | 208.5 | 209.5 | 208.5 | NO
| NG | 114 | 16 | 27 | 27 | 87.6 | 19.64 | 50 | 78.6 | 39.1 | 64.4 | 49.4 | 208.6 | 207.8 | 207.8 | NO
| NG | 101 | 100 | 30 | 27 | 148.1 | 5.59 | 50 | 78.6 | 39.1 | 74.5 | 45.6 | 207.7 | 220.9 | 207.7 | NO
| NG | 40 | 61 | 53 | 11 | 81.2 | 32.93 | 50 | 78.6 | 39.1 | 54 | 76.2 | 221.6 | 151.4 | 151.4 | NO
| NG | 11 | 8 | 0 | 0 | 57.1 | 22.24 | 50 | 78.6 | 39.1 | 62.3 | 66.2 | 208.5 | 208.9 | 208.5 | NO
| NG | 16 | 15 | 27 | 27 | 87.6 | 16.41 | 50 | 78.6 | 39.1 | 66.7 | 47.9 | 208.5 | 211.3 | 208.5 | NO
| NG | 100 | 103 | 30 | 27 | 148.1 | 4.58 | 50 | 78.6 | 39.1 | 75.3 | 44.4 | 207.7 | 220.4 | 207.7 | NO
| NG | 61 | 62 | 53 | 11 | 81.2 | 31.12 | 50 | 78.6 | 39.1 | 55.3 | 75.3 | 221.6 | 150.8 | 150.8 | NO
| NG | 8 | 9 | 0 | 0 | 57.1 | 21.88 | 50 | 78.6 | 39.1 | 62.6 | 65.7 | 208.5 | 208.6 | 208.5 | NO
| NG | 15 | 17 | 27 | 27 | 87.6 | 14.89 | 50 | 78.6 | 39.1 | 67.8 | 47.3 | 208.4 | 212.6 | 208.4 | NO
| NG | 103 | 102 | 30 | 27 | 148.1 | 4.58 | 50 | 78.6 | 39.1 | 75.3 | 44.4 | 207.7 | 220.4 | 207.7 | NO
| NG | 62 | 97 | 53 | 11 | 81.2 | 29.63 | 50 | 78.6 | 39.1 | 56.4 | 73.7 | 221.6 | 153.5 | 153.5 | NO
| NG | 9 | 22 | 0 | 0 | 57.1 | 20.18 | 50 | 78.6 | 39.1 | 63.8 | 63.5 | 208.5 | 210.9 | 208.5 | NO
| NG | 17 | 79 | 27 | 27 | 87.6 | 13.18 | 50 | 78.6 | 39.1 | 69 | 47 | 208.4 | 213.2 | 208.4 | NO
| NG | 102 | 34 | 30 | 27 | 148.1 | 3.03 | 50 | 78.6 | 39.1 | 76.4 | 42.6 | 207.6 | 222.2 | 207.6 | NO
| NG | 97 | 80 | 53 | 11 | 81.2 | 28.38 | 50 | 78.6 | 39.1 | 57.3 | 71.4 | 221.5 | 158.3 | 158.3 | NO
| NG | 22 | 116 | 0 | 0 | 57.1 | 18.27 | 50 | 78.6 | 39.1 | 65.2 | 61.1 | 208.4 | 215.6 | 208.4 | NO
| NG | 79 | 78 | 27 | 27 | 87.6 | 12.64 | 50 | 78.6 | 39.1 | 69.4 | 46.3 | 208.3 | 214.8 | 208.3 | NO
| NG | 34 | 33 | 30 | 27 | 148.1 | 3.03 | 50 | 78.6 | 39.1 | 76.4 | 42.6 | 207.6 | 222.2 | 207.6 | NO
| NG | 80 | 81 | 53 | 11 | 81.2 | 27.12 | 50 | 78.6 | 39.1 | 58.2 | 68.6 | 221.4 | 166.4 | 166.4 | NO
| NG | 116 | 21 | 0 | 0 | 57.1 | 16.34 | 50 | 78.6 | 39.1 | 66.6 | 56.8 | 208.3 | 216.4 | 208.3 | NO
| NG | 78 | 19 | 27 | 27 | 87.6 | 12.64 | 50 | 78.6 | 39.1 | 69.4 | 46.3 | 208.3 | 214.8 | 208.3 | NO
| NG | 33 | 31 | 30 | 27 | 148.1 | 2.68 | 50 | 78.6 | 39.1 | 76.6 | 42.2 | 207.5 | 222.2 | 207.5 | NO
| NG | 81 | 82 | 53 | 11 | 81.2 | 27.12 | 50 | 78.6 | 39.1 | 58.2 | 68.6 | 221.4 | 166.4 | 166.4 | NO
| NG | 21 | 20 | 0 | 0 | 57.1 | 14.84 | 50 | 78.6 | 39.1 | 67.7 | 56.8 | 208.3 | 216.5 | 208.3 | NO
| NG | 19 | 18 | 27 | 27 | 87.6 | 11.09 | 50 | 78.6 | 39.1 | 70.5 | 45.1 | 208.2 | 217.5 | 208.2 | NO
| NG | 31 | 32 | 30 | 27 | 148.1 | 1.99 | 50 | 78.6 | 39.1 | 77.1 | 41.4 | 207.5 | 222.4 | 207.5 | NO
| NG | 82 | 109 | 53 | 11 | 81.2 | 27.12 | 50 | 78.6 | 39.1 | 58.2 | 68.6 | 221.4 | 166.4 | 166.4 | NO
| NG | 20 | 7 | 0 | 0 | 57.1 | 13.32 | 50 | 78.6 | 39.1 | 68.8 | 54.9 | 208.2 | 217.4 | 208.2 | NO
| NG | 18 | 24 | 27 | 27 | 87.6 | 10.93 | 50 | 78.6 | 39.1 | 70.6 | 44.9 | 208.1 | 217.9 | 208.1 | NO
| NG | 32 | 91 | 30 | 27 | 148.1 | 1.66 | 50 | 78.6 | 39.1 | 77.4 | 41 | 207.5 | 222.4 | 207.5 | NO
| NG | 109 | 60 | 53 | 11 | 81.2 | 26.79 | 50 | 78.6 | 39.1 | 58.4 | 68.6 | 221.4 | 166.4 | 166.4 | NO
| NG | 7 | 6 | 0 | 0 | 57.1 | 12.13 | 50 | 78.6 | 39.1 | 69.6 | 53.5 | 208.2 | 218.9 | 208.2 | NO
| NG | 24 | 25 | 27 | 27 | 87.6 | 8.82 | 50 | 78.6 | 39.1 | 72.1 | 44.9 | 208.1 | 217.9 | 208.1 | NO
| NG | 91 | 92 | 30 | 27 | 148.1 | 1.2 | 50 | 78.6 | 39.1 | 77.7 | 40.4 | 207.5 | 222.5 | 207.5 | NO
| NG | 60 | 58 | 53 | 11 | 81.2 | 18.81 | 50 | 78.6 | 39.1 | 64.3 | 55.3 | 219 | 207.1 | 207.1 | NO
| NG | 6 | 5 | 0 | 0 | 57.1 | 10.93 | 50 | 78.6 | 39.1 | 70.5 | 52 | 208 | 218.8 | 208 | NO
| NG | 25 | 26 | 27 | 27 | 87.6 | 8.82 | 50 | 78.6 | 39.1 | 72.1 | 44.9 | 208.1 | 217.9 | 208.1 | NO
| NG | 92 | 83 | 30 | 27 | 148.1 | 1.2 | 50 | 78.6 | 39.1 | 77.7 | 40.4 | 207.5 | 222.5 | 207.5 | NO
| NG | 58 | 59 | 53 | 11 | 81.2 | 18.81 | 50 | 78.6 | 39.1 | 64.3 | 55.3 | 219 | 207.1 | 207.1 | NO
| NG | 5 | 4 | 0 | 0 | 57.1 | 10.86 | 50 | 78.6 | 39.1 | 70.6 | 51.9 | 208 | 218.7 | 208 | NO
| NG | 26 | 86 | 27 | 27 | 87.6 | 6.29 | 50 | 78.6 | 39.1 | 74 | 42.8 | 207.9 | 221.8 | 207.9 | NO
| NG | 83 | 30 | 30 | 27 | 148.1 | 1.09 | 50 | 78.6 | 39.1 | 77.8 | 40.3 | 207.5 | 222.5 | 207.5 | NO
| NG | 59 | 115 | 53 | 11 | 81.2 | 18.27 | 50 | 78.6 | 39.1 | 64.7 | 54.5 | 219 | 208.4 | 208.4 | NO
| NG | 4 | 3 | 0 | 0 | 57.1 | 9.93 | 50 | 78.6 | 39.1 | 71.2 | 50.8 | 208 | 221.1 | 208 | NO
| NG | 86 | 85 | 27 | 27 | 87.6 | 4.32 | 50 | 78.6 | 39.1 | 75.4 | 41.9 | 207.8 | 222.5 | 207.8 | NO
1 | OK | 115 | 95 | 53 | 11 | 81.2 | 17.34 | 50 | 78.6 | 39.1 | 65.4 | 53.3 | 218.4 | 210.1 | 210.1 | YES
| NG | 3 | 1 | 0 | 0 | 57.1 | 8.98 | 50 | 78.6 | 39.1 | 71.9 | 49.6 | 208 | 221.4 | 208 | NO
| NG | 85 | 74 | 27 | 27 | 87.6 | 3.72 | 50 | 78.6 | 39.1 | 75.9 | 41.1 | 207.7 | 222.5 | 207.7 | NO
2 | OK | 95 | 57 | 53 | 11 | 81.2 | 17.34 | 50 | 78.6 | 39.1 | 65.4 | 53.3 | 218.4 | 210.1 | 210.1 | YES
| NG | 1 | 2 | 0 | 0 | 57.1 | 8.36 | 50 | 78.6 | 39.1 | 72.4 | 48.9 | 207.9 | 221.4 | 207.9 | NO
| NG | 74 | 73 | 27 | 27 | 87.6 | 1.72 | 50 | 78.6 | 39.1 | 77.3 | 40.3 | 207.6 | 222.5 | 207.6 | NO
3 | OK | 57 | 42 | 53 | 11 | 81.2 | 16.25 | 50 | 78.6 | 39.1 | 66.2 | 52.5 | 218.4 | 210.3 | 210.3 | YES
| NG | 2 | 89 | 0 | 0 | 57.1 | 7.69 | 50 | 78.6 | 39.1 | 72.9 | 48.1 | 207.8 | 221.3 | 207.8 | NO
| NG | 73 | 72 | 27 | 27 | 87.6 | 1.17 | 50 | 78.6 | 39.1 | 77.7 | 39.9 | 207.5 | 222.5 | 207.5 | NO
| NG | 42 | 43 | 53 | 11 | 81.2 | 12.29 | 50 | 78.6 | 39.1 | 69.1 | 50.6 | 219.2 | 209.9 | 209.9 | NO
| NG | 89 | 90 | 0 | 0 | 57.1 | 5.17 | 50 | 78.6 | 39.1 | 74.7 | 45.1 | 207.8 | 222.1 | 207.8 | NO
| NG | 72 | 77 | 27 | 27 | 87.6 | 0.72 | 50 | 78.6 | 39.1 | 78 | 39.9 | 207.5 | 222.5 | 207.5 | NO
| NG | 43 | 107 | 53 | 11 | 81.2 | 10.95 | 50 | 78.6 | 39.1 | 70.1 | 50.6 | 219.6 | 209.9 | 209.9 | NO
| NG | 90 | 75 | 0 | 0 | 57.1 | 3.36 | 50 | 78.6 | 39.1 | 76.1 | 43 | 207.6 | 222.1 | 207.6 | NO
| NG | 77 | 28 | 27 | 27 | 87.6 | 0.72 | 50 | 78.6 | 39.1 | 78 | 39.9 | 207.5 | 222.5 | 207.5 | NO
4 | OK | 107 | 108 | 53 | 11 | 81.2 | 4.56 | 50 | 78.6 | 39.1 | 75 | 44.5 | 214.1 | 220.1 | 214.1 | YES
5 | OK | 107 | 46 | 122 | 40 | 115.7 | 6.39 | 50 | 78.6 | 39.1 | 73.6 | 46.8 | 213 | 219.1 | 213 | YES
| NG | 75 | 76 | 0 | 0 | 57.1 | 2.86 | 50 | 78.6 | 39.1 | 76.4 | 42.4 | 207.6 | 222.1 | 207.6 | NO
| NG | 28 | 27 | 27 | 27 | 87.6 | 0.72 | 50 | 78.6 | 39.1 | 78 | 39.9 | 207.5 | 222.5 | 207.5 | NO
6 | ** OPTIMAL ** | 108 | 44 | 53 | 11 | 81.2 | 4.07 | 50 | 78.6 | 39.1 | 75 | 43.9 | 214.1 | 221 | 214.1 | YES
7 | OK | 46 | 47 | 49 | 40 | 147.3 | 5.16 | 50 | 78.6 | 39.1 | 74.5 | 43.7 | 213.2 | 218.6 | 213.2 | YES
| NG | 46 | 117 | 122 | 40 | 115.7 | 1.08 | 50 | 78.6 | 39.1 | 77.8 | 40.4 | 207.3 | 222.5 | 207.3 | NO
| NG | 76 | 0 | 0 | 0 | 57.1 | 2.44 | 50 | 78.6 | 39.1 | 76.8 | 41.9 | 207.6 | 222.1 | 207.6 | NO
| NG | 27 | 29 | 29 | 27 | 89.4 | 0.57 | 50 | 78.6 | 39.1 | 78.2 | 39.7 | 207.5 | 222.5 | 207.5 | NO
8 | OK | 44 | 45 | 53 | 11 | 81.2 | 4.07 | 50 | 78.6 | 39.1 | 75.3 | 43.9 | 213.3 | 221 | 213.3 | YES
9 | OK | 47 | 96 | 49 | 40 | 147.3 | 3.96 | 50 | 78.6 | 39.1 | 75.4 | 43.7 | 214 | 218.6 | 214 | YES
| NG | 117 | 121 | 122 | 40 | 115.7 | 0.91 | 50 | 78.6 | 39.1 | 77.9 | 40.1 | 207.4 | 222.8 | 207.4 | NO
| NG | 29 | 12 | 12 | 27 | 116.7 | 0.05 | 50 | 78.6 | 39.1 | 78.5 | 39.1 | 207.4 | 222.5 | 207.4 | NO
10 | OK | 45 | 87 | 53 | 11 | 81.2 | 3.59 | 50 | 78.6 | 39.1 | 75.7 | 43.3 | 212.8 | 221.5 | 212.8 | YES
11 | OK | 96 | 48 | 49 | 40 | 147.3 | 3.89 | 50 | 78.6 | 39.1 | 75.5 | 43.7 | 214 | 218.6 | 214 | YES
12 | OK | 87 | 88 | 53 | 11 | 81.2 | 3.59 | 50 | 78.6 | 39.1 | 75.7 | 43.3 | 212.8 | 221.5 | 212.8 | YES
| NG | 48 | 49 | 49 | 40 | 147.3 | 0.91 | 50 | 78.6 | 39.1 | 77.8 | 40.1 | 208.8 | 222.6 | 208.8 | NO
13 | OK | 88 | 52 | 53 | 11 | 81.2 | 3.11 | 50 | 78.6 | 39.1 | 76.1 | 42.8 | 212.1 | 222.2 | 212.1 | YES
14 | OK | 52 | 53 | 53 | 11 | 81.2 | 2.95 | 50 | 78.6 | 39.1 | 76.2 | 42.6 | 212.1 | 222.2 | 212.1 | YES
15 | OK | 53 | 54 | 56 | 40 | 83 | 2.47 | 50 | 78.6 | 39.1 | 76.6 | 42 | 211 | 223 | 211 | YES
16 | OK | 54 | 55 | 56 | 40 | 83 | 1.95 | 50 | 78.6 | 39.1 | 77 | 41.4 | 211 | 222.8 | 211 | YES
| NG | 55 | 56 | 56 | 40 | 83 | 1 | 50 | 78.6 | 39.1 | 77.8 | 40.2 | 208.7 | 222.7 | 208.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 37-017969
TR_B (available) | 49-003614
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 78.6
TR_B Baseline Loading% | 39.1
Total Scenarios Evaluated | 100
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 108
Switch Child Node | 44
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 81.2
Load Transferred (kW) | 4.07
TR_A Loading After (%) | 75
TR_B Loading After (%) | 43.9
Minimum Voltage (V) | 214.1