## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 36 | 35 | 23 | 0 | 1.1 | 33.43 | 95 | 78.6 | 52.1 | 53.7 | 77.8 | 221.7 | 200.9 | 200.9 | NO
| NG | 36 | 41 | 69 | 23 | 0.7 | 34.28 | 95 | 78.6 | 52.1 | 53.7 | 78.1 | 209.2 | 208.8 | 208.8 | NO
| NG | 36 | 38 | 38 | 23 | 75 | 22.42 | 95 | 78.6 | 52.1 | 62.4 | 68.8 | 208.6 | 214 | 208.6 | NO
| NG | 36 | 94 | 94 | 23 | 71.3 | 17.5 | 95 | 78.6 | 52.1 | 65.9 | 65.1 | 207.9 | 213.8 | 207.9 | NO
| NG | 35 | 99 | 23 | 0 | 1.1 | 33.43 | 95 | 78.6 | 52.1 | 53.7 | 77.8 | 221.7 | 200.9 | 200.9 | NO
| NG | 41 | 66 | 69 | 23 | 0.7 | 5.01 | 95 | 78.6 | 52.1 | 75 | 55.8 | 207.7 | 215.6 | 207.7 | NO
| NG | 41 | 14 | 14 | 23 | 114.3 | 28.62 | 95 | 78.6 | 52.1 | 57.8 | 73.7 | 208.9 | 211 | 208.9 | NO
| NG | 38 | 37 | 37 | 23 | 100.8 | 20.82 | 95 | 78.6 | 52.1 | 63.5 | 67.6 | 208.6 | 213.6 | 208.6 | NO
| NG | 94 | 93 | 30 | 56 | 109.6 | 17.42 | 50 | 78.6 | 52.1 | 66 | 67 | 207.9 | 180.7 | 180.7 | NO
| NG | 99 | 64 | 23 | 0 | 1.1 | 33.43 | 95 | 78.6 | 52.1 | 53.7 | 77.8 | 221.7 | 200.9 | 200.9 | NO
| NG | 66 | 98 | 69 | 23 | 0.7 | 3.6 | 95 | 78.6 | 52.1 | 76 | 54.7 | 207.7 | 215.7 | 207.7 | NO
| NG | 66 | 119 | 119 | 23 | 138.1 | 1.41 | 95 | 78.6 | 52.1 | 77.6 | 53.1 | 207.5 | 215.9 | 207.5 | NO
| NG | 37 | 118 | 118 | 23 | 106.1 | 20.82 | 95 | 78.6 | 52.1 | 63.5 | 67.6 | 208.6 | 213.6 | 208.6 | NO
| NG | 93 | 105 | 30 | 56 | 109.6 | 6.55 | 50 | 78.6 | 52.1 | 73.8 | 57.1 | 207.8 | 212.1 | 207.8 | NO
| NG | 64 | 63 | 23 | 0 | 1.1 | 0.15 | 95 | 78.6 | 52.1 | 78.5 | 52.2 | 207.4 | 215.9 | 207.4 | NO
| NG | 64 | 39 | 39 | 23 | 21 | 33.28 | 95 | 78.6 | 52.1 | 53.8 | 77.8 | 221.7 | 198.1 | 198.1 | NO
| NG | 98 | 104 | 69 | 23 | 0.7 | 3.6 | 95 | 78.6 | 52.1 | 76 | 54.7 | 207.7 | 215.7 | 207.7 | NO
| NG | 118 | 114 | 114 | 23 | 107.5 | 20.3 | 95 | 78.6 | 52.1 | 63.9 | 67.2 | 208.6 | 213.6 | 208.6 | NO
| NG | 105 | 101 | 30 | 56 | 109.6 | 5.96 | 50 | 78.6 | 52.1 | 74.3 | 56.7 | 207.7 | 214.2 | 207.7 | NO
| NG | 39 | 40 | 40 | 23 | 28.8 | 33.25 | 95 | 78.6 | 52.1 | 53.8 | 77.8 | 221.7 | 198.1 | 198.1 | NO
| NG | 104 | 67 | 69 | 23 | 0.7 | 2.46 | 95 | 78.6 | 52.1 | 76.8 | 53.9 | 207.5 | 215.8 | 207.5 | NO
| NG | 114 | 16 | 16 | 23 | 108.2 | 19.64 | 95 | 78.6 | 52.1 | 64.4 | 66.7 | 208.6 | 213.4 | 208.6 | NO
| NG | 101 | 100 | 30 | 56 | 109.6 | 5.59 | 50 | 78.6 | 52.1 | 74.5 | 56.4 | 207.7 | 213.9 | 207.7 | NO
| NG | 40 | 61 | 48 | 52 | 33.9 | 32.93 | 50 | 78.6 | 52.1 | 54 | 83.9 | 221.6 | 137.8 | 137.8 | NO
| NG | 67 | 68 | 69 | 23 | 0.7 | 0.36 | 95 | 78.6 | 52.1 | 78.3 | 52.4 | 207.5 | 215.9 | 207.5 | NO
| NG | 16 | 15 | 15 | 23 | 117.8 | 16.41 | 95 | 78.6 | 52.1 | 66.7 | 64.3 | 208.5 | 214.9 | 208.5 | NO
| NG | 100 | 103 | 30 | 56 | 109.6 | 4.58 | 50 | 78.6 | 52.1 | 75.3 | 55.6 | 207.7 | 214.8 | 207.7 | NO
| NG | 61 | 62 | 48 | 52 | 33.9 | 31.12 | 50 | 78.6 | 52.1 | 55.3 | 82.8 | 221.6 | 133.3 | 133.3 | NO
| NG | 15 | 17 | 12 | 56 | 123 | 14.89 | 50 | 78.6 | 52.1 | 67.8 | 57.8 | 208.4 | 196 | 196 | NO
| NG | 103 | 102 | 30 | 56 | 109.6 | 4.58 | 50 | 78.6 | 52.1 | 75.3 | 55.6 | 207.7 | 214.8 | 207.7 | NO
| NG | 62 | 97 | 48 | 52 | 33.9 | 29.63 | 50 | 78.6 | 52.1 | 56.4 | 81.1 | 221.6 | 135.8 | 135.8 | NO
| NG | 17 | 79 | 12 | 56 | 123 | 13.18 | 50 | 78.6 | 52.1 | 69 | 57.6 | 208.4 | 196.8 | 196.8 | NO
| NG | 102 | 34 | 30 | 56 | 109.6 | 3.03 | 50 | 78.6 | 52.1 | 76.4 | 54.4 | 207.6 | 215.6 | 207.6 | NO
| NG | 97 | 80 | 48 | 52 | 33.9 | 28.38 | 50 | 78.6 | 52.1 | 57.3 | 79.2 | 221.5 | 143.3 | 143.3 | NO
| NG | 79 | 78 | 12 | 56 | 123 | 12.64 | 50 | 78.6 | 52.1 | 69.4 | 57.1 | 208.3 | 199 | 199 | NO
| NG | 34 | 33 | 30 | 56 | 109.6 | 3.03 | 50 | 78.6 | 52.1 | 76.4 | 54.4 | 207.6 | 215.6 | 207.6 | NO
| NG | 80 | 81 | 48 | 52 | 33.9 | 27.12 | 50 | 78.6 | 52.1 | 58.2 | 76.9 | 221.4 | 154.4 | 154.4 | NO
| NG | 78 | 19 | 12 | 56 | 123 | 12.64 | 50 | 78.6 | 52.1 | 69.4 | 57.1 | 208.3 | 199 | 199 | NO
| NG | 33 | 31 | 30 | 56 | 109.6 | 2.68 | 50 | 78.6 | 52.1 | 76.6 | 54.1 | 207.5 | 215.3 | 207.5 | NO
| NG | 81 | 82 | 48 | 52 | 33.9 | 27.12 | 50 | 78.6 | 52.1 | 58.2 | 76.9 | 221.4 | 154.4 | 154.4 | NO
| NG | 19 | 18 | 12 | 56 | 123 | 11.09 | 50 | 78.6 | 52.1 | 70.5 | 56.2 | 208.2 | 202.9 | 202.9 | NO
| NG | 31 | 32 | 30 | 56 | 109.6 | 1.99 | 50 | 78.6 | 52.1 | 77.1 | 53.6 | 207.5 | 215.3 | 207.5 | NO
| NG | 82 | 109 | 48 | 52 | 33.9 | 27.12 | 50 | 78.6 | 52.1 | 58.2 | 76.9 | 221.4 | 154.4 | 154.4 | NO
| NG | 18 | 24 | 12 | 56 | 123 | 10.93 | 50 | 78.6 | 52.1 | 70.6 | 56.1 | 208.1 | 203.4 | 203.4 | NO
| NG | 32 | 91 | 30 | 56 | 109.6 | 1.66 | 50 | 78.6 | 52.1 | 77.4 | 53.4 | 207.5 | 215.1 | 207.5 | NO
| NG | 109 | 60 | 48 | 52 | 33.9 | 26.79 | 50 | 78.6 | 52.1 | 58.4 | 76.7 | 221.4 | 153.8 | 153.8 | NO
| NG | 24 | 25 | 12 | 56 | 123 | 8.82 | 50 | 78.6 | 52.1 | 72.1 | 56.1 | 208.1 | 203.4 | 203.4 | NO
| NG | 91 | 92 | 30 | 56 | 109.6 | 1.2 | 50 | 78.6 | 52.1 | 77.7 | 53.1 | 207.5 | 215.2 | 207.5 | NO
| NG | 60 | 58 | 48 | 52 | 33.9 | 18.81 | 50 | 78.6 | 52.1 | 64.3 | 67.4 | 219 | 198.2 | 198.2 | NO
| NG | 25 | 26 | 12 | 56 | 123 | 8.82 | 50 | 78.6 | 52.1 | 72.1 | 56.1 | 208.1 | 203.4 | 203.4 | NO
| NG | 92 | 83 | 30 | 56 | 109.6 | 1.2 | 50 | 78.6 | 52.1 | 77.7 | 53.1 | 207.5 | 215.2 | 207.5 | NO
| NG | 58 | 59 | 48 | 52 | 33.9 | 18.81 | 50 | 78.6 | 52.1 | 64.3 | 67.4 | 219 | 198.2 | 198.2 | NO
| NG | 26 | 86 | 12 | 56 | 123 | 6.29 | 50 | 78.6 | 52.1 | 74 | 54.6 | 207.9 | 208.9 | 207.9 | NO
| NG | 83 | 30 | 30 | 56 | 109.6 | 1.09 | 50 | 78.6 | 52.1 | 77.8 | 53 | 207.5 | 215.1 | 207.5 | NO
| NG | 59 | 115 | 48 | 52 | 33.9 | 18.27 | 50 | 78.6 | 52.1 | 64.7 | 66.9 | 219 | 200.9 | 200.9 | NO
| NG | 86 | 85 | 12 | 56 | 123 | 4.32 | 50 | 78.6 | 52.1 | 75.4 | 54 | 207.8 | 211.4 | 207.8 | NO
| NG | 115 | 95 | 48 | 52 | 33.9 | 17.34 | 50 | 78.6 | 52.1 | 65.4 | 66.1 | 218.4 | 202.1 | 202.1 | NO
| NG | 85 | 74 | 12 | 56 | 123 | 3.72 | 50 | 78.6 | 52.1 | 75.9 | 53.5 | 207.7 | 213.2 | 207.7 | NO
| NG | 95 | 57 | 48 | 52 | 33.9 | 17.34 | 50 | 78.6 | 52.1 | 65.4 | 66.1 | 218.4 | 202.1 | 202.1 | NO
| NG | 74 | 73 | 12 | 56 | 123 | 1.72 | 50 | 78.6 | 52.1 | 77.3 | 52.9 | 207.6 | 215.3 | 207.6 | NO
| NG | 57 | 42 | 48 | 52 | 33.9 | 16.25 | 50 | 78.6 | 52.1 | 66.2 | 65.1 | 218.4 | 203.5 | 203.5 | NO
| NG | 73 | 72 | 12 | 56 | 123 | 1.17 | 50 | 78.6 | 52.1 | 77.7 | 52.7 | 207.5 | 215.8 | 207.5 | NO
| NG | 73 | 106 | 111 | 85 | 138 | 0.55 | 50 | 78.6 | 52.1 | 78.2 | 52.5 | 207.5 | 215.9 | 207.5 | NO
| NG | 42 | 43 | 48 | 52 | 33.9 | 12.29 | 50 | 78.6 | 52.1 | 69.1 | 62 | 219.2 | 201 | 201 | NO
| NG | 72 | 77 | 12 | 56 | 123 | 0.72 | 50 | 78.6 | 52.1 | 78 | 52.7 | 207.5 | 215.8 | 207.5 | NO
| NG | 106 | 70 | 111 | 85 | 138 | 0.44 | 50 | 78.6 | 52.1 | 78.3 | 52.4 | 207.5 | 215.9 | 207.5 | NO
| NG | 43 | 107 | 48 | 52 | 33.9 | 10.95 | 50 | 78.6 | 52.1 | 70.1 | 61 | 219.6 | 199.8 | 199.8 | NO
| NG | 77 | 28 | 12 | 56 | 123 | 0.72 | 50 | 78.6 | 52.1 | 78 | 52.7 | 207.5 | 215.8 | 207.5 | NO
| NG | 70 | 71 | 111 | 85 | 138 | 0.34 | 50 | 78.6 | 52.1 | 78.3 | 52.4 | 207.5 | 215.9 | 207.5 | NO
| NG | 107 | 108 | 108 | 49 | 64.7 | 4.56 | 50 | 78.6 | 52.1 | 75 | 55.7 | 214.1 | 209.8 | 209.8 | NO
1 | OK | 107 | 46 | 48 | 52 | 33.9 | 6.39 | 50 | 78.6 | 52.1 | 73.6 | 57.1 | 213 | 210.5 | 210.5 | YES
| NG | 28 | 27 | 12 | 56 | 123 | 0.72 | 50 | 78.6 | 52.1 | 78 | 52.7 | 207.5 | 215.8 | 207.5 | NO
| NG | 71 | 113 | 111 | 85 | 138 | 0.26 | 50 | 78.6 | 52.1 | 78.4 | 52.3 | 207.5 | 215.9 | 207.5 | NO
2 | OK | 108 | 44 | 44 | 49 | 67.8 | 4.07 | 50 | 78.6 | 52.1 | 75 | 55.4 | 214.1 | 210.7 | 210.7 | YES
3 | OK | 46 | 47 | 48 | 52 | 33.9 | 5.16 | 50 | 78.6 | 52.1 | 74.5 | 56.1 | 213.2 | 210.2 | 210.2 | YES
| NG | 46 | 117 | 117 | 49 | 50.4 | 1.08 | 50 | 78.6 | 52.1 | 77.8 | 53 | 207.3 | 214.8 | 207.3 | NO
| NG | 27 | 29 | 12 | 56 | 123 | 0.57 | 50 | 78.6 | 52.1 | 78.2 | 52.5 | 207.5 | 215.8 | 207.5 | NO
| NG | 113 | 112 | 111 | 85 | 138 | 0.25 | 50 | 78.6 | 52.1 | 78.4 | 52.3 | 207.5 | 215.9 | 207.5 | NO
4 | OK | 44 | 45 | 45 | 56 | 74.3 | 4.07 | 50 | 78.6 | 52.1 | 75.3 | 55.3 | 213.3 | 211.6 | 211.6 | YES
| NG | 47 | 96 | 48 | 52 | 33.9 | 3.96 | 50 | 78.6 | 52.1 | 75.4 | 55.3 | 214 | 209.4 | 209.4 | NO
| NG | 117 | 121 | 121 | 49 | 74.8 | 0.91 | 50 | 78.6 | 52.1 | 77.9 | 52.8 | 207.4 | 214.8 | 207.4 | NO
| NG | 29 | 12 | 12 | 56 | 123 | 0.05 | 50 | 78.6 | 52.1 | 78.5 | 52.1 | 207.4 | 215.9 | 207.4 | NO
| NG | 112 | 110 | 111 | 85 | 138 | 0.02 | 50 | 78.6 | 52.1 | 78.6 | 52.1 | 207.4 | 215.9 | 207.4 | NO
5 | OK | 45 | 87 | 87 | 56 | 86.2 | 3.59 | 50 | 78.6 | 52.1 | 75.7 | 54.9 | 212.8 | 212.2 | 212.2 | YES
| NG | 96 | 48 | 48 | 52 | 33.9 | 3.89 | 50 | 78.6 | 52.1 | 75.5 | 55.2 | 214 | 209.3 | 209.3 | NO
6 | ** OPTIMAL ** | 87 | 88 | 88 | 56 | 109.5 | 3.59 | 50 | 78.6 | 52.1 | 75.7 | 54.9 | 212.8 | 212.2 | 212.2 | YES
| NG | 48 | 49 | 49 | 52 | 78.2 | 0.91 | 50 | 78.6 | 52.1 | 77.8 | 52.8 | 208.8 | 215.8 | 208.8 | NO
7 | OK | 48 | 84 | 84 | 52 | 34.3 | 2.98 | 50 | 78.6 | 52.1 | 76.2 | 54.5 | 212.7 | 211.1 | 211.1 | YES
8 | OK | 88 | 52 | 52 | 56 | 112.3 | 3.11 | 50 | 78.6 | 52.1 | 76.1 | 54.6 | 212.1 | 213 | 212.1 | YES
9 | OK | 84 | 51 | 51 | 52 | 43.8 | 2.31 | 50 | 78.6 | 52.1 | 76.7 | 53.9 | 211.2 | 213.1 | 211.2 | YES
10 | OK | 52 | 53 | 55 | 49 | 123.4 | 2.95 | 50 | 78.6 | 52.1 | 76.2 | 54.4 | 212.1 | 212.8 | 212.1 | YES
| NG | 51 | 50 | 50 | 52 | 67.7 | 0.72 | 50 | 78.6 | 52.1 | 78 | 52.7 | 209.2 | 215.6 | 209.2 | NO
11 | OK | 53 | 54 | 55 | 49 | 123.4 | 2.47 | 50 | 78.6 | 52.1 | 76.6 | 54.1 | 211 | 214.2 | 211 | YES
12 | OK | 54 | 55 | 55 | 49 | 123.4 | 1.95 | 50 | 78.6 | 52.1 | 77 | 53.6 | 211 | 214.2 | 211 | YES
| NG | 55 | 56 | 56 | 49 | 123.5 | 1 | 50 | 78.6 | 52.1 | 77.8 | 52.9 | 208.7 | 215.8 | 208.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 37-017969
TR_B (available) | 68-014335
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 78.6
TR_B Baseline Loading% | 52.1
Total Scenarios Evaluated | 95
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 87
Switch Child Node | 88
Tie Node (TR_A side) | 88
Tie Node (TR_B side) | 56
Tie Line Distance (m) | 109.5
Load Transferred (kW) | 3.59
TR_A Loading After (%) | 75.7
TR_B Loading After (%) | 54.9
Minimum Voltage (V) | 212.2