## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 39 | 16 | 143 | 0 | 8.2 | 7.37 | 50 | 77.9 | 38.2 | 72.3 | 43.8 | 210.5 | 217 | 210.5 | YES
2 | ** OPTIMAL ** | 16 | 17 | 143 | 0 | 8.2 | 6.67 | 50 | 77.9 | 38.2 | 72.8 | 43.8 | 210.6 | 217 | 210.6 | YES
| NG | 17 | 122 | 143 | 0 | 8.2 | 3.67 | 50 | 77.9 | 38.2 | 75 | 43.8 | 208.7 | 217 | 208.7 | NO
| NG | 122 | 135 | 143 | 0 | 8.2 | 3.25 | 50 | 77.9 | 38.2 | 75.4 | 43.8 | 208.8 | 217 | 208.8 | NO
| NG | 135 | 136 | 143 | 0 | 8.2 | 3.25 | 50 | 77.9 | 38.2 | 75.4 | 43.8 | 208.8 | 217 | 208.8 | NO
| NG | 136 | 137 | 143 | 0 | 8.2 | 1.27 | 50 | 77.9 | 38.2 | 76.9 | 43.8 | 209 | 217 | 209 | NO
| NG | 137 | 142 | 143 | 0 | 8.2 | 0.97 | 50 | 77.9 | 38.2 | 77.1 | 43.8 | 209 | 217 | 209 | NO
| NG | 142 | 143 | 143 | 0 | 8.2 | 0.79 | 50 | 77.9 | 38.2 | 77.3 | 42.8 | 209.1 | 217.2 | 209.1 | NO
| NG | 142 | 200 | 200 | 0 | 61.3 | 0.18 | 50 | 77.9 | 38.2 | 77.7 | 39.3 | 209.3 | 218.1 | 209.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 37-018628
TR_B (available) | 28-016838
TR_A Rated kVA | 160
TR_B Rated kVA | 20
TR_A Baseline Loading% | 77.9
TR_B Baseline Loading% | 38.2
Total Scenarios Evaluated | 9
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 17
Tie Node (TR_A side) | 143
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 8.2
Load Transferred (kW) | 6.67
TR_A Loading After (%) | 72.8
TR_B Loading After (%) | 43.8
Minimum Voltage (V) | 210.6