## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 86 | 87 | 25 | 14 | 28.3 | 27.28 | 50 | 77.9 | 6.6 | 40.8 | 40.1 | 207.7 | 203.9 | 203.9 | NO
1 | OK | 86 | 173 | 52 | 10 | 122.1 | 27.67 | 50 | 77.9 | 6.6 | 56.7 | 20.3 | 210.9 | 211.9 | 210.9 | YES
2 | OK | 86 | 193 | 170 | 14 | 27 | 11.33 | 50 | 77.9 | 6.6 | 69.2 | 9.9 | 211.3 | 222.9 | 211.3 | YES
| NG | 87 | 88 | 25 | 14 | 28.3 | 26.32 | 50 | 77.9 | 6.6 | 41.5 | 38.8 | 207.7 | 207.6 | 207.6 | NO
| NG | 173 | 52 | 52 | 10 | 122.1 | 2.69 | 50 | 77.9 | 6.6 | 75.8 | 7.4 | 209.6 | 229.1 | 209.6 | NO
3 | ** OPTIMAL ** | 193 | 163 | 170 | 14 | 27 | 11.33 | 50 | 77.9 | 6.6 | 69.2 | 9.9 | 211.3 | 222.9 | 211.3 | YES
| NG | 88 | 130 | 25 | 14 | 28.3 | 24.6 | 50 | 77.9 | 6.6 | 42.7 | 36.5 | 207.7 | 209 | 207.7 | NO
| NG | 52 | 51 | 51 | 10 | 124.3 | 2.22 | 50 | 77.9 | 6.6 | 0 | 9.2 | 8.2 | 228.8 | 8.2 | NO
| NG | 163 | 164 | 170 | 14 | 27 | 9.39 | 50 | 77.9 | 6.6 | 70.7 | 9.9 | 210 | 222.9 | 210 | NO
| NG | 130 | 97 | 25 | 14 | 28.3 | 23.45 | 50 | 77.9 | 6.6 | 43.5 | 35 | 207.5 | 210.7 | 207.5 | NO
| NG | 51 | 217 | 217 | 10 | 139.2 | 1.96 | 50 | 77.9 | 6.6 | 76.3 | 8.9 | 47.5 | 228.8 | 47.5 | NO
| NG | 164 | 167 | 170 | 14 | 27 | 8.92 | 50 | 77.9 | 6.6 | 71.1 | 9.9 | 209.7 | 222.9 | 209.7 | NO
| NG | 97 | 98 | 25 | 14 | 28.3 | 21.83 | 50 | 77.9 | 6.6 | 44.7 | 32.9 | 207.3 | 209.6 | 207.3 | NO
| NG | 217 | 29 | 29 | 10 | 149.3 | 1.66 | 50 | 77.9 | 6.6 | 76.3 | 8.5 | 47.5 | 229 | 47.5 | NO
| NG | 167 | 165 | 45 | 14 | 130.7 | 7.61 | 50 | 77.9 | 6.6 | 72.1 | 15.4 | 209.7 | 226.8 | 209.7 | NO
| NG | 167 | 171 | 170 | 14 | 27 | 1.31 | 50 | 77.9 | 6.6 | 76.9 | 6.6 | 209.4 | 229.1 | 209.4 | NO
| NG | 98 | 6 | 25 | 14 | 28.3 | 21.5 | 50 | 77.9 | 6.6 | 44.9 | 32.5 | 207.3 | 210.7 | 207.3 | NO
| NG | 165 | 48 | 45 | 14 | 130.7 | 7.61 | 50 | 77.9 | 6.6 | 72.1 | 15.4 | 209.7 | 226.8 | 209.7 | NO
| NG | 171 | 196 | 170 | 14 | 27 | 1.31 | 50 | 77.9 | 6.6 | 76.9 | 6.6 | 209.4 | 229.1 | 209.4 | NO
4 | OK | 6 | 131 | 25 | 14 | 28.3 | 17.16 | 50 | 77.9 | 6.6 | 60.1 | 27 | 210.4 | 216.4 | 210.4 | YES
| NG | 48 | 47 | 45 | 14 | 130.7 | 7.61 | 50 | 77.9 | 6.6 | 72.1 | 15.4 | 209.7 | 226.8 | 209.7 | NO
5 | OK | 131 | 103 | 25 | 14 | 28.3 | 17.16 | 50 | 77.9 | 6.6 | 60.1 | 26 | 210.4 | 216 | 210.4 | YES
| NG | 47 | 27 | 45 | 14 | 130.7 | 6.49 | 50 | 77.9 | 6.6 | 72.3 | 14.1 | 48.5 | 227.7 | 48.5 | NO
6 | OK | 103 | 102 | 25 | 14 | 28.3 | 15.63 | 50 | 77.9 | 6.6 | 61.2 | 25.1 | 210.3 | 215.8 | 210.3 | YES
| NG | 27 | 26 | 45 | 14 | 130.7 | 6.34 | 50 | 77.9 | 6.6 | 72.3 | 14 | 48.4 | 227.7 | 48.4 | NO
| NG | 102 | 104 | 25 | 14 | 28.3 | 14.86 | 50 | 77.9 | 6.6 | 65.5 | 24.2 | 210 | 217.8 | 210 | NO
| NG | 26 | 148 | 45 | 14 | 130.7 | 5.95 | 50 | 77.9 | 6.6 | 73.3 | 13.5 | 209.7 | 227.6 | 209.7 | NO
| NG | 104 | 105 | 25 | 14 | 28.3 | 14.2 | 50 | 77.9 | 6.6 | 66 | 23.4 | 209.9 | 217.9 | 209.9 | NO
| NG | 148 | 44 | 45 | 14 | 130.7 | 5.21 | 50 | 77.9 | 6.6 | 73.9 | 12.7 | 209.7 | 227.4 | 209.7 | NO
| NG | 105 | 106 | 25 | 14 | 28.3 | 13.45 | 50 | 77.9 | 6.6 | 66.5 | 22.4 | 209.9 | 219.3 | 209.9 | NO
| NG | 44 | 45 | 45 | 14 | 130.7 | 2.46 | 50 | 77.9 | 6.6 | 76 | 9.5 | 209.5 | 228.2 | 209.5 | NO
| NG | 106 | 15 | 25 | 14 | 28.3 | 12.78 | 50 | 77.9 | 6.6 | 67 | 21.6 | 209.9 | 219 | 209.9 | NO
| NG | 45 | 5 | 5 | 14 | 145.4 | 1.71 | 50 | 77.9 | 6.6 | 76.6 | 8.6 | 209.4 | 228.8 | 209.4 | NO
| NG | 15 | 14 | 25 | 14 | 28.3 | 7.56 | 50 | 77.9 | 6.6 | 71.1 | 15.4 | 209.6 | 222.6 | 209.6 | NO
| NG | 5 | 3 | 3 | 14 | 154.8 | 1.23 | 50 | 77.9 | 6.6 | 76.9 | 8 | 209.4 | 229.1 | 209.4 | NO
| NG | 14 | 21 | 25 | 14 | 28.3 | 5.1 | 50 | 77.9 | 6.6 | 73.7 | 12.5 | 209.7 | 227.9 | 209.7 | NO
| NG | 21 | 218 | 25 | 14 | 28.3 | 4.54 | 50 | 77.9 | 6.6 | 74.3 | 11.9 | 209.6 | 227.8 | 209.6 | NO
| NG | 218 | 115 | 25 | 14 | 28.3 | 4.03 | 50 | 77.9 | 6.6 | [5 empty] | NO | TR_A sim: loading 2963% (degenerate)
| NG | 115 | 116 | 25 | 14 | 28.3 | 3.17 | 50 | 77.9 | 6.6 | 75.4 | 10.3 | 209.5 | 228.8 | 209.5 | NO
| NG | 116 | 161 | 25 | 14 | 28.3 | 2.89 | 50 | 77.9 | 6.6 | 75.6 | 10 | 209.5 | 228.8 | 209.5 | NO
| NG | 161 | 117 | 25 | 14 | 28.3 | 2.68 | 50 | 77.9 | 6.6 | 75.8 | 9.7 | 209.5 | 228.9 | 209.5 | NO
| NG | 117 | 118 | 25 | 14 | 28.3 | 1.94 | 50 | 77.9 | 6.6 | 76.4 | 8.9 | 209.4 | 228.9 | 209.4 | NO
| NG | 118 | 119 | 25 | 14 | 28.3 | 1.38 | 50 | 77.9 | 6.6 | 76.8 | 8.2 | 209.4 | 228.9 | 209.4 | NO
| NG | 119 | 22 | 25 | 14 | 28.3 | 1.2 | 50 | 77.9 | 6.6 | 76.9 | 8 | 209.4 | 228.9 | 209.4 | NO
| NG | 22 | 23 | 23 | 14 | 104.9 | 0.71 | 50 | 77.9 | 6.6 | 77.3 | 7.4 | 209.4 | 228.9 | 209.4 | NO
| NG | 22 | 41 | 25 | 14 | 28.3 | 0.49 | 50 | 77.9 | 6.6 | 77.5 | 7.2 | 209.4 | 229.1 | 209.4 | NO
| NG | 41 | 25 | 25 | 14 | 28.3 | 0.25 | 50 | 77.9 | 6.6 | 77.7 | 6.9 | 209.4 | 229.1 | 209.4 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 37-018628
TR_B (available) | 64-014193
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 77.9
TR_B Baseline Loading% | 6.6
Total Scenarios Evaluated | 47
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 193
Switch Child Node | 163
Tie Node (TR_A side) | 170
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 27
Load Transferred (kW) | 11.33
TR_A Loading After (%) | 69.2
TR_B Loading After (%) | 9.9
Minimum Voltage (V) | 211.3