## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 26 | 29 | 30 | 1.1 | 1.81 | 50 | 85.5 | 62.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 7 | 6 | 6 | 30 | 140 | 4.95 | 50 | 85.5 | 62.5 | 66.2 | 81.8 | 217.7 | 214.9 | 214.9 | NO
| NG | 22 | 23 | 23 | 9 | 102.3 | 5 | 50 | 85.5 | 62.5 | 65.5 | 82.8 | 219.6 | 212.2 | 212.2 | NO
1 | OK | 23 | 31 | 31 | 9 | 125 | 3.08 | 50 | 85.5 | 62.5 | 73.3 | 74.8 | 214.5 | 213.8 | 213.8 | YES
2 | ** OPTIMAL ** | 31 | 32 | 32 | 9 | 138.7 | 2.01 | 50 | 85.5 | 62.5 | 77.4 | 70.5 | 214.9 | 217.3 | 214.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-000416
TR_B (available) | 47-003011
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.5
TR_B Baseline Loading% | 62.5
Total Scenarios Evaluated | 5
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 31
Switch Child Node | 32
Tie Node (TR_A side) | 32
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 138.7
Load Transferred (kW) | 2.01
TR_A Loading After (%) | 77.4
TR_B Loading After (%) | 70.5
Minimum Voltage (V) | 214.9