## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 37 | 31 | 30 | 12 | 4.5 | 10.67 | 50 | 81 | 16.6 | 39.8 | 58.5 | 216.7 | 218 | 216.7 | YES
2 | OK | 37 | 42 | 42 | 12 | 71.4 | 10.14 | 50 | 81 | 16.6 | 41.2 | 57.6 | 222.3 | 210.7 | 210.7 | YES
3 | OK | 31 | 30 | 30 | 12 | 4.5 | 8.72 | 50 | 81 | 16.6 | 47.2 | 50.8 | 216.7 | 218.8 | 216.7 | YES
4 | OK | 30 | 29 | 29 | 12 | 12.6 | 8.72 | 50 | 81 | 16.6 | 47.2 | 50.7 | 216.7 | 218.9 | 216.7 | YES
5 | ** OPTIMAL ** | 29 | 7 | 10 | 6 | 30.7 | 8.68 | 50 | 81 | 16.6 | 47.4 | 27.7 | 216.7 | 221.4 | 216.7 | YES
6 | OK | 7 | 8 | 10 | 6 | 30.7 | 7.18 | 50 | 81 | 16.6 | 53.1 | 27.7 | 215.5 | 221.4 | 215.5 | YES
7 | OK | 8 | 9 | 10 | 6 | 30.7 | 5.22 | 50 | 81 | 16.6 | 60.7 | 24.2 | 214.7 | 222.9 | 214.7 | YES
8 | OK | 9 | 10 | 10 | 6 | 30.7 | 5.22 | 50 | 81 | 16.6 | 60.7 | 24.2 | 214.7 | 222.9 | 214.7 | YES
9 | OK | 10 | 4 | 4 | 6 | 46.4 | 4.21 | 50 | 81 | 16.6 | 64.6 | 24.2 | 213.9 | 223 | 213.9 | YES
10 | OK | 4 | 5 | 5 | 6 | 77.7 | 1.2 | 50 | 81 | 16.6 | 76.4 | 21.3 | 212.1 | 224.4 | 212.1 | YES
11 | OK | 4 | 6 | 6 | 6 | 58.2 | 3.01 | 50 | 81 | 16.6 | 69.2 | 19.5 | 213.9 | 225.3 | 213.9 | YES
12 | OK | 5 | 11 | 11 | 6 | 110.6 | 0.49 | 50 | 81 | 16.6 | 79.1 | 18.5 | 212.1 | 225.7 | 212.1 | YES
13 | OK | 6 | 13 | 13 | 7 | 80.4 | 0.88 | 50 | 81 | 16.6 | 77.5 | 17.6 | 212.6 | 226.1 | 212.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-000768
TR_B (available) | 60-022686
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81
TR_B Baseline Loading% | 16.6
Total Scenarios Evaluated | 13
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 7
Tie Node (TR_A side) | 10
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 30.7
Load Transferred (kW) | 8.68
TR_A Loading After (%) | 47.4
TR_B Loading After (%) | 27.7
Minimum Voltage (V) | 216.7