## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 37 | 42 | 22 | 52 | 0.6 | 10.14 | 50 | 81 | 36.8 | 41.2 | 49.6 | 222.3 | 204.6 | 204.6 | NO
| NG | 42 | 32 | 22 | 52 | 0.6 | 10.06 | 50 | 81 | 36.8 | 41.5 | 49.5 | 222.3 | 204.5 | 204.5 | NO
| NG | 32 | 33 | 22 | 52 | 0.6 | 10.03 | 50 | 81 | 36.8 | 41.6 | 49.5 | 222.3 | 204.5 | 204.5 | NO
| NG | 33 | 34 | 22 | 52 | 0.6 | 9.73 | 50 | 81 | 36.8 | 42.7 | 49.1 | 222.3 | 204.1 | 204.1 | NO
| NG | 34 | 35 | 22 | 52 | 0.6 | 9.17 | 50 | 81 | 36.8 | 44.9 | 48.3 | 222.3 | 203.6 | 203.6 | NO
| NG | 35 | 36 | 22 | 52 | 0.6 | 8.33 | 50 | 81 | 36.8 | 48.1 | 47.3 | 222.3 | 202.7 | 202.7 | NO
| NG | 36 | 28 | 22 | 52 | 0.6 | 6.18 | 50 | 81 | 36.8 | 56.5 | 44.7 | 220.4 | 200.7 | 200.7 | NO
| NG | 28 | 27 | 22 | 52 | 0.6 | 6.15 | 50 | 81 | 36.8 | 56.6 | 44.7 | 220.3 | 200.7 | 200.7 | NO
1 | OK | 27 | 26 | 22 | 52 | 0.6 | 1.5 | 50 | 81 | 36.8 | 75 | 38.6 | 213.8 | 218.1 | 213.8 | YES
2 | OK | 26 | 25 | 22 | 52 | 0.6 | 1.11 | 50 | 81 | 36.8 | 76.5 | 38.1 | 213.9 | 218.1 | 213.9 | YES
3 | OK | 25 | 1 | 22 | 52 | 0.6 | 0.93 | 50 | 81 | 36.8 | 77.2 | 37.9 | 214 | 218 | 214 | YES
4 | OK | 1 | 0 | 0 | 52 | 58.7 | 0.79 | 50 | 81 | 36.8 | 77.8 | 37.7 | 214 | 218 | 214 | YES
5 | ** OPTIMAL ** | 0 | 24 | 24 | 52 | 60.4 | 0.79 | 50 | 81 | 36.8 | 77.8 | 36.8 | 214 | 218.7 | 214 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-000768
TR_B (available) | 64-022397
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 81
TR_B Baseline Loading% | 36.8
Total Scenarios Evaluated | 13
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 24
Tie Node (TR_A side) | 24
Tie Node (TR_B side) | 52
Tie Line Distance (m) | 60.4
Load Transferred (kW) | 0.79
TR_A Loading After (%) | 77.8
TR_B Loading After (%) | 36.8
Minimum Voltage (V) | 214