## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 25 | 19 | 4 | 8.5 | 22.63 | 50 | 96.7 | 41.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 25 | 45 | 19 | 4 | 8.5 | 22.28 | 50 | 96.7 | 41.3 | 6.2 | 54.3 | 230 | 178.2 | 178.2 | NO
| NG | 45 | 34 | 19 | 4 | 8.5 | 21.99 | 50 | 96.7 | 41.3 | 7.3 | 54.3 | 230 | 178.2 | 178.2 | NO
| NG | 34 | 35 | 19 | 4 | 8.5 | 21.7 | 50 | 96.7 | 41.3 | 7.3 | 53.9 | 230 | 179.4 | 179.4 | NO
| NG | 35 | 39 | 19 | 4 | 8.5 | 21.53 | 50 | 96.7 | 41.3 | 9 | 53.7 | 229.7 | 180 | 180 | NO
| NG | 39 | 28 | 19 | 4 | 8.5 | 21.53 | 50 | 96.7 | 41.3 | 9 | 53.7 | 229.7 | 180 | 180 | NO
| NG | 28 | 26 | 19 | 4 | 8.5 | 19.86 | 50 | 96.7 | 41.3 | 15.4 | 52.9 | 228.6 | 182.8 | 182.8 | NO
| NG | 26 | 27 | 19 | 4 | 8.5 | 18.37 | 50 | 96.7 | 41.3 | 21.1 | 51.3 | 226.9 | 188.2 | 188.2 | NO
| NG | 27 | 16 | 19 | 4 | 8.5 | 15.91 | 50 | 96.7 | 41.3 | 30.6 | 50.6 | 226.1 | 190.7 | 190.7 | NO
| NG | 16 | 14 | 19 | 4 | 8.5 | 15.43 | 50 | 96.7 | 41.3 | 32.5 | 50.6 | 226.1 | 190.7 | 190.7 | NO
| NG | 14 | 15 | 19 | 4 | 8.5 | 15.28 | 50 | 96.7 | 41.3 | 33 | 50.6 | 226 | 190.7 | 190.7 | NO
| NG | 15 | 24 | 19 | 4 | 8.5 | 5.54 | 50 | 96.7 | 41.3 | 72.7 | 43.8 | 204.5 | 215.9 | 204.5 | NO
1 | ** OPTIMAL ** | 15 | 11 | 11 | 114 | 130.1 | 9.74 | 50 | 96.7 | 41.3 | 55 | 48.8 | 216.1 | 210.6 | 210.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-006187
TR_B (available) | 49-005559
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 96.7
TR_B Baseline Loading% | 41.3
Total Scenarios Evaluated | 13
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 11
Tie Node (TR_A side) | 11
Tie Node (TR_B side) | 114
Tie Line Distance (m) | 130.1
Load Transferred (kW) | 9.74
TR_A Loading After (%) | 55
TR_B Loading After (%) | 48.8
Minimum Voltage (V) | 210.6