## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 9 | 45 | 2 | 9 | 7.33 | 50 | 84.1 | 17.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 9 | 8 | 45 | 2 | 9 | 6.64 | 50 | 84.1 | 17.8 | 58.6 | 32.8 | 214.4 | 218.3 | 214.4 | YES
2 | OK | 8 | 47 | 45 | 2 | 9 | 5.26 | 50 | 84.1 | 17.8 | 63.9 | 29.9 | 213.9 | 220.3 | 213.9 | YES
3 | OK | 47 | 54 | 45 | 2 | 9 | 5.26 | 50 | 84.1 | 17.8 | 63.9 | 29.9 | 213.9 | 220.3 | 213.9 | YES
4 | OK | 54 | 46 | 45 | 2 | 9 | 5.26 | 50 | 84.1 | 17.8 | 63.9 | 29.9 | 213.9 | 220.3 | 213.9 | YES
5 | OK | 46 | 6 | 45 | 2 | 9 | 4.45 | 50 | 84.1 | 17.8 | 67 | 26.7 | 213.9 | 222.6 | 213.9 | YES
6 | OK | 6 | 5 | 45 | 2 | 9 | 3.33 | 50 | 84.1 | 17.8 | 71.2 | 24.5 | 213.5 | 224.1 | 213.5 | YES
7 | OK | 5 | 7 | 30 | 2 | 106.2 | 3.07 | 50 | 84.1 | 17.8 | 72.2 | 24.4 | 213.3 | 225.2 | 213.3 | YES
8 | OK | 7 | 40 | 30 | 2 | 106.2 | 2.7 | 50 | 84.1 | 17.8 | 73.7 | 24.4 | 213 | 225.2 | 213 | YES
9 | OK | 40 | 30 | 30 | 2 | 106.2 | 2.22 | 50 | 84.1 | 17.8 | 75.5 | 22.5 | 213 | 226.3 | 213 | YES
10 | OK | 30 | 31 | 31 | 2 | 106.3 | 1.86 | 50 | 84.1 | 17.8 | 76.9 | 17.8 | 212.8 | 227.9 | 212.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-006639
TR_B (available) | 50-001372
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 84.1
TR_B Baseline Loading% | 17.8
Total Scenarios Evaluated | 11
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 45
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 9
Load Transferred (kW) | 6.64
TR_A Loading After (%) | 58.6
TR_B Loading After (%) | 32.8
Minimum Voltage (V) | 214.4