## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 9 | 45 | 6 | 47.2 | 7.33 | 50 | 84.1 | 18.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 9 | 8 | 45 | 6 | 47.2 | 6.64 | 50 | 84.1 | 18.5 | 58.6 | 33.5 | 214.4 | 215.4 | 214.4 | YES
2 | OK | 8 | 47 | 45 | 6 | 47.2 | 5.26 | 50 | 84.1 | 18.5 | 63.9 | 30.6 | 213.9 | 217.7 | 213.9 | YES
3 | OK | 47 | 54 | 45 | 6 | 47.2 | 5.26 | 50 | 84.1 | 18.5 | 63.9 | 30.6 | 213.9 | 217.7 | 213.9 | YES
4 | OK | 54 | 46 | 45 | 6 | 47.2 | 5.26 | 50 | 84.1 | 18.5 | 63.9 | 30.6 | 213.9 | 217.7 | 213.9 | YES
5 | OK | 46 | 6 | 45 | 6 | 47.2 | 4.45 | 50 | 84.1 | 18.5 | 67 | 27.3 | 213.9 | 220.2 | 213.9 | YES
6 | OK | 6 | 5 | 45 | 6 | 47.2 | 3.33 | 50 | 84.1 | 18.5 | 71.2 | 25.1 | 213.5 | 220.7 | 213.5 | YES
7 | OK | 5 | 7 | 31 | 6 | 140.4 | 3.07 | 50 | 84.1 | 18.5 | 72.2 | 25 | 213.3 | 220.7 | 213.3 | YES
8 | OK | 7 | 40 | 31 | 6 | 140.4 | 2.7 | 50 | 84.1 | 18.5 | 73.7 | 25 | 213 | 220.7 | 213 | YES
9 | OK | 40 | 30 | 31 | 6 | 140.4 | 2.22 | 50 | 84.1 | 18.5 | 75.5 | 23.2 | 213 | 221.1 | 213 | YES
10 | OK | 30 | 31 | 31 | 6 | 140.4 | 1.86 | 50 | 84.1 | 18.5 | 76.9 | 18.5 | 212.8 | 222 | 212.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-006639
TR_B (available) | 63-035711
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 84.1
TR_B Baseline Loading% | 18.5
Total Scenarios Evaluated | 11
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 45
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 47.2
Load Transferred (kW) | 6.64
TR_A Loading After (%) | 58.6
TR_B Loading After (%) | 33.5
Minimum Voltage (V) | 214.4