## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 20 | 4 | 91 | 1 | 167.7 | 1.83 | 50 | 70.3 | 56.7 | 68.1 | 62.2 | 213.9 | 211.9 | 211.9 | YES
2 | OK | 9 | 13 | 10 | 7 | 158.9 | 5.78 | 50 | 70.3 | 56.7 | 63.5 | 79.5 | 214.1 | 210.7 | 210.7 | YES
3 | OK | 4 | 29 | 91 | 1 | 167.7 | 1.68 | 50 | 70.3 | 56.7 | 68.3 | 61.6 | 213.9 | 212 | 212 | YES
4 | OK | 13 | 14 | 10 | 7 | 158.9 | 1.6 | 50 | 70.3 | 56.7 | 68.4 | 62.9 | 213.7 | 212.6 | 212.6 | YES
5 | ** OPTIMAL ** | 29 | 86 | 90 | 1 | 168.2 | 0.15 | 50 | 70.3 | 56.7 | 70.2 | 56.7 | 213.4 | 213 | 213 | YES
6 | OK | 29 | 88 | 91 | 1 | 167.7 | 1.12 | 50 | 70.3 | 56.7 | 68.8 | 61 | 213.3 | 212.1 | 212.1 | YES
7 | OK | 14 | 58 | 10 | 7 | 158.9 | 0.47 | 50 | 70.3 | 56.7 | 69.8 | 58.5 | 213.4 | 212.6 | 212.6 | YES
8 | OK | 86 | 90 | 90 | 1 | 168.2 | 0.15 | 50 | 70.3 | 56.7 | 70.2 | 56.7 | 213.4 | 213 | 213 | YES
9 | OK | 88 | 98 | 91 | 1 | 167.7 | 1.12 | 50 | 70.3 | 56.7 | 68.8 | 61 | 213.3 | 212.1 | 212.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-011188
TR_B (available) | 45-023541
TR_A Rated kVA | 100
TR_B Rated kVA | 30
TR_A Baseline Loading% | 70.3
TR_B Baseline Loading% | 56.7
Total Scenarios Evaluated | 9
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 86
Tie Node (TR_A side) | 90
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 168.2
Load Transferred (kW) | 0.15
TR_A Loading After (%) | 70.2
TR_B Loading After (%) | 56.7
Minimum Voltage (V) | 213