## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 20 | 80 | 18 | 66.6 | 14 | 50 | 70.3 | 26.3 | 53.5 | 67.9 | 216.5 | 159.3 | 159.3 | NO
| NG | 20 | 21 | 80 | 18 | 66.6 | 7.1 | 50 | 70.3 | 26.3 | 61.7 | 45.4 | 216.2 | 191.3 | 191.3 | NO
1 | OK | 21 | 60 | 80 | 18 | 66.6 | 2.86 | 50 | 70.3 | 26.3 | 66 | 33.4 | 212.8 | 213.4 | 212.8 | YES
2 | OK | 60 | 63 | 80 | 18 | 66.6 | 0.01 | 50 | 70.3 | 26.3 | 68.7 | 26.4 | 213.2 | 223.2 | 213.2 | YES
3 | OK | 60 | 67 | 66 | 18 | 68.4 | 1.36 | 50 | 70.3 | 26.3 | 68.7 | 26.3 | 213.2 | 223.2 | 213.2 | YES
4 | OK | 67 | 68 | 66 | 18 | 68.4 | 1.36 | 50 | 70.3 | 26.3 | 68.7 | 26.3 | 213.2 | 223.2 | 213.2 | YES
5 | OK | 68 | 69 | 66 | 18 | 68.4 | 1.35 | 50 | 70.3 | 26.3 | 68.7 | 26.3 | 213.2 | 223.2 | 213.2 | YES
6 | OK | 69 | 70 | 66 | 18 | 68.4 | 1.35 | 50 | 70.3 | 26.3 | 68.7 | 26.3 | 213.2 | 223.2 | 213.2 | YES
7 | OK | 70 | 65 | 66 | 18 | 68.4 | 0.34 | 50 | 70.3 | 26.3 | 69.9 | 26.3 | 213.4 | 223.2 | 213.4 | YES
8 | ** OPTIMAL ** | 65 | 66 | 66 | 18 | 68.4 | 0.34 | 50 | 70.3 | 26.3 | 69.9 | 26.3 | 213.4 | 223.2 | 213.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-011188
TR_B (available) | 53-010767
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 70.3
TR_B Baseline Loading% | 26.3
Total Scenarios Evaluated | 10
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 65
Switch Child Node | 66
Tie Node (TR_A side) | 66
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 68.4
Load Transferred (kW) | 0.34
TR_A Loading After (%) | 69.9
TR_B Loading After (%) | 26.3
Minimum Voltage (V) | 213.4