## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 5 | 20 | 32 | 1 | 20.4 | 14 | 50 | 70.3 | 6.8 | 53.5 | 29.7 | 216.5 | 215.8 | 215.8 | YES
2 | OK | 5 | 102 | 51 | 1 | 1 | 14.68 | 50 | 70.3 | 6.8 | 52.8 | 33.1 | 216.7 | 213.8 | 213.8 | YES
3 | OK | 20 | 21 | 32 | 1 | 20.4 | 7.1 | 50 | 70.3 | 6.8 | 61.7 | 23.9 | 216.2 | 219.4 | 216.2 | YES
4 | ** OPTIMAL ** | 102 | 0 | 51 | 1 | 1 | 13.81 | 50 | 70.3 | 6.8 | 53.8 | 29.5 | 216.5 | 216.4 | 216.4 | YES
5 | OK | 102 | 61 | 62 | 4 | 1.5 | 0.02 | 50 | 70.3 | 6.8 | 70.3 | 6.8 | 213.4 | 228.6 | 213.4 | YES
6 | OK | 21 | 22 | 101 | 1 | 138.3 | 1.39 | 50 | 70.3 | 6.8 | 68.7 | 9.2 | 213.2 | 227.4 | 213.2 | YES
7 | OK | 21 | 60 | 32 | 1 | 20.4 | 2.86 | 50 | 70.3 | 6.8 | 66 | 18 | 212.8 | 222.2 | 212.8 | YES
8 | OK | 0 | 1 | 51 | 1 | 1 | 10.48 | 50 | 70.3 | 6.8 | 57.7 | 24.9 | 216.2 | 219.5 | 216.2 | YES
9 | OK | 22 | 101 | 101 | 1 | 138.3 | 1.39 | 50 | 70.3 | 6.8 | 68.7 | 9.2 | 213.2 | 227.4 | 213.2 | YES
| NG | 60 | 64 | 64 | 0 | 135.5 | 1.09 | 50 | 70.3 | 6.8 | 345.5 | 11 | 19.1 | 226.5 | 19.1 | NO
10 | OK | 1 | 36 | 51 | 1 | 1 | 9.53 | 50 | 70.3 | 6.8 | 58.8 | 22.1 | 216.1 | 221.2 | 216.1 | YES
11 | OK | 36 | 59 | 51 | 1 | 1 | 8.14 | 50 | 70.3 | 6.8 | 60.5 | 22.1 | 214.9 | 221.2 | 214.9 | YES
12 | OK | 59 | 30 | 51 | 1 | 1 | 8.14 | 50 | 70.3 | 6.8 | 60.5 | 22.1 | 214.9 | 221.2 | 214.9 | YES
13 | OK | 30 | 17 | 51 | 1 | 1 | 6.72 | 50 | 70.3 | 6.8 | 62.2 | 20.9 | 213.8 | 221.8 | 213.8 | YES
14 | OK | 17 | 16 | 51 | 1 | 1 | 4.43 | 50 | 70.3 | 6.8 | 65 | 11.9 | 214 | 226.3 | 214 | YES
15 | OK | 16 | 2 | 51 | 1 | 1 | 1.84 | 50 | 70.3 | 6.8 | 68.1 | 10.3 | 214 | 227 | 214 | YES
16 | OK | 2 | 39 | 51 | 1 | 1 | 1.35 | 50 | 70.3 | 6.8 | 68.7 | 9.4 | 214 | 227.3 | 214 | YES
17 | OK | 39 | 51 | 51 | 1 | 1 | 0.67 | 50 | 70.3 | 6.8 | 69.5 | 6.8 | 214.1 | 228.6 | 214.1 | YES
18 | OK | 39 | 99 | 99 | 0 | 90.6 | 0.68 | 50 | 70.3 | 6.8 | 69.5 | 9.4 | 213.4 | 227.4 | 213.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-011188
TR_B (available) | 60-030527
TR_A Rated kVA | 100
TR_B Rated kVA | 30
TR_A Baseline Loading% | 70.3
TR_B Baseline Loading% | 6.8
Total Scenarios Evaluated | 19
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 102
Switch Child Node | 0
Tie Node (TR_A side) | 51
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 1
Load Transferred (kW) | 13.81
TR_A Loading After (%) | 53.8
TR_B Loading After (%) | 29.5
Minimum Voltage (V) | 216.4