## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 62 | 32 | 32 | 6 | 78.4 | 1.21 | 50 | 80.2 | 49.7 | 64.3 | 53.5 | 216.2 | 219.1 | 216.2 | YES
2 | OK | 62 | 72 | 72 | 1 | 6.4 | 0.48 | 50 | 80.2 | 49.7 | 78.3 | 49.7 | 216 | 221.1 | 216 | YES
3 | OK | 62 | 21 | 8 | 51 | 1.2 | 8.45 | 50 | 80.2 | 49.7 | 45.6 | 66.8 | 222.4 | 216.8 | 216.8 | YES
4 | OK | 32 | 33 | 33 | 6 | 82.7 | 0.9 | 50 | 80.2 | 49.7 | 65.4 | 53.3 | 216 | 219.2 | 216 | YES
5 | OK | 73 | 3 | 3 | 4 | 55.7 | 5.45 | 50 | 80.2 | 49.7 | 59.1 | 71 | 220.2 | 217.7 | 217.7 | YES
6 | OK | 73 | 13 | 64 | 42 | 38.8 | 5.18 | 50 | 80.2 | 49.7 | 60.4 | 58.2 | 217.7 | 221.1 | 217.7 | YES
7 | OK | 21 | 20 | 8 | 51 | 1.2 | 8.01 | 50 | 80.2 | 49.7 | 47.3 | 65 | 222.1 | 217.7 | 217.7 | YES
8 | OK | 33 | 18 | 18 | 6 | 83.5 | 0.81 | 50 | 80.2 | 49.7 | 65.4 | 53 | 216 | 219.4 | 216 | YES
9 | OK | 3 | 4 | 4 | 4 | 55.9 | 5.45 | 50 | 80.2 | 49.7 | 59.1 | 71 | 220.2 | 217.8 | 217.8 | YES
10 | OK | 13 | 12 | 35 | 42 | 59.2 | 0.94 | 50 | 80.2 | 49.7 | 76.5 | 53.4 | 216.8 | 221.1 | 216.8 | YES
11 | OK | 13 | 34 | 58 | 6 | 81.7 | 3.53 | 50 | 80.2 | 49.7 | 66.9 | 61.9 | 216.4 | 212.4 | 212.4 | YES
12 | OK | 13 | 75 | 64 | 42 | 38.8 | 0.56 | 50 | 80.2 | 49.7 | 78 | 51.9 | 216.5 | 221.1 | 216.5 | YES
13 | OK | 20 | 61 | 8 | 51 | 1.2 | 7.76 | 50 | 80.2 | 49.7 | 48.2 | 65 | 222.1 | 217.7 | 217.7 | YES
14 | OK | 18 | 19 | 19 | 6 | 95.9 | 0.39 | 50 | 80.2 | 49.7 | 67.4 | 51.3 | 216 | 220.3 | 216 | YES
15 | OK | 4 | 57 | 57 | 4 | 71.5 | 5.29 | 50 | 80.2 | 49.7 | 59.7 | 70.4 | 220.1 | 218.4 | 218.4 | YES
16 | OK | 12 | 11 | 35 | 42 | 59.2 | 0.94 | 50 | 80.2 | 49.7 | 76.5 | 51.9 | 216.8 | 221.1 | 216.8 | YES
17 | OK | 34 | 55 | 58 | 6 | 81.7 | 0.66 | 50 | 80.2 | 49.7 | 77.8 | 50.3 | 216.4 | 220.8 | 216.4 | YES
18 | OK | 34 | 2 | 2 | 51 | 148.9 | 2.87 | 50 | 80.2 | 49.7 | 69.1 | 60.9 | 216 | 219.7 | 216 | YES
19 | OK | 75 | 76 | 64 | 42 | 38.8 | 0.56 | 50 | 80.2 | 49.7 | 78 | 51.9 | 216.5 | 221.1 | 216.5 | YES
20 | OK | 61 | 43 | 8 | 51 | 1.2 | 7.22 | 50 | 80.2 | 49.7 | 50.3 | 65 | 222.1 | 217.7 | 217.7 | YES
21 | OK | 57 | 56 | 56 | 4 | 74.4 | 3.63 | 50 | 80.2 | 49.7 | 66.1 | 63.8 | 218.8 | 221.2 | 218.8 | YES
22 | OK | 11 | 14 | 35 | 42 | 59.2 | 0.55 | 50 | 80.2 | 49.7 | 78 | 51.9 | 216.5 | 221.1 | 216.5 | YES
23 | OK | 55 | 54 | 54 | 4 | 112.5 | 0.29 | 50 | 80.2 | 49.7 | 78.3 | 50.9 | 216.4 | 221.1 | 216.4 | YES
24 | OK | 55 | 45 | 58 | 6 | 81.7 | 0.37 | 50 | 80.2 | 49.7 | 78.7 | 50.3 | 216.2 | 220.8 | 216.2 | YES
25 | OK | 76 | 52 | 64 | 42 | 38.8 | 0.56 | 50 | 80.2 | 49.7 | 78 | 51.9 | 216.5 | 221.1 | 216.5 | YES
26 | OK | 43 | 28 | 8 | 51 | 1.2 | 7.22 | 50 | 80.2 | 49.7 | 52.1 | 65 | 222.1 | 217.7 | 217.7 | YES
27 | OK | 14 | 35 | 35 | 42 | 59.2 | 0.08 | 50 | 80.2 | 49.7 | 79.9 | 50.1 | 216.1 | 221.1 | 216.1 | YES
28 | OK | 45 | 46 | 58 | 6 | 81.7 | 0.13 | 50 | 80.2 | 49.7 | 79.7 | 50.3 | 216 | 220.8 | 216 | YES
29 | OK | 52 | 64 | 64 | 42 | 38.8 | 0.56 | 50 | 80.2 | 49.7 | 78 | 51.4 | 216.5 | 221.1 | 216.5 | YES
30 | OK | 28 | 24 | 8 | 51 | 1.2 | 7.22 | 50 | 80.2 | 49.7 | 52.1 | 65 | 222.1 | 217.7 | 217.7 | YES
31 | OK | 24 | 9 | 8 | 51 | 1.2 | 6.93 | 50 | 80.2 | 49.7 | 53.2 | 65 | 222.1 | 217.7 | 217.7 | YES
32 | OK | 9 | 7 | 8 | 51 | 1.2 | 6.93 | 50 | 80.2 | 49.7 | 53.2 | 65 | 222.1 | 217.7 | 217.7 | YES
33 | OK | 7 | 8 | 8 | 51 | 1.2 | 0.22 | 50 | 80.2 | 49.7 | 79.3 | 50.6 | 216.4 | 221.1 | 216.4 | YES
34 | OK | 7 | 23 | 17 | 42 | 1.4 | 6.71 | 50 | 80.2 | 49.7 | 54.1 | 64.1 | 222 | 219.4 | 219.4 | YES
35 | ** OPTIMAL ** | 23 | 22 | 17 | 42 | 1.4 | 6.27 | 50 | 80.2 | 49.7 | 55.7 | 62.4 | 221.6 | 220.6 | 220.6 | YES
36 | OK | 22 | 38 | 17 | 42 | 1.4 | 4.76 | 50 | 80.2 | 49.7 | 61.6 | 62.4 | 221.6 | 220.6 | 220.6 | YES
37 | OK | 38 | 37 | 47 | 39 | 1.6 | 1.51 | 50 | 80.2 | 49.7 | 74.3 | 55.5 | 215.9 | 221.1 | 215.9 | YES
38 | OK | 38 | 42 | 17 | 42 | 1.4 | 3.25 | 50 | 80.2 | 49.7 | 67.5 | 62.4 | 219.9 | 220.6 | 219.9 | YES
39 | OK | 37 | 47 | 47 | 39 | 1.6 | 1.24 | 50 | 80.2 | 49.7 | 75.3 | 54.5 | 215.9 | 221.1 | 215.9 | YES
40 | OK | 42 | 50 | 17 | 42 | 1.4 | 2.56 | 50 | 80.2 | 49.7 | 70.1 | 59.6 | 220.1 | 221.1 | 220.1 | YES
41 | OK | 47 | 48 | 48 | 39 | 10.7 | 0.98 | 50 | 80.2 | 49.7 | 76.3 | 53.5 | 215.9 | 221.1 | 215.9 | YES
42 | OK | 50 | 51 | 17 | 42 | 1.4 | 1.64 | 50 | 80.2 | 49.7 | 73.7 | 56.1 | 220.4 | 221.1 | 220.4 | YES
43 | OK | 48 | 25 | 25 | 39 | 16.8 | 0.91 | 50 | 80.2 | 49.7 | 76.6 | 53.2 | 215.9 | 221.1 | 215.9 | YES
44 | OK | 51 | 17 | 17 | 42 | 1.4 | 1.38 | 50 | 80.2 | 49.7 | 74.7 | 55 | 219.9 | 221.1 | 219.9 | YES
45 | OK | 25 | 26 | 26 | 39 | 108.1 | 0.2 | 50 | 80.2 | 49.7 | 79.4 | 50.5 | 216 | 221.1 | 216 | YES
46 | OK | 25 | 31 | 31 | 39 | 35.9 | 0.71 | 50 | 80.2 | 49.7 | 77.4 | 52.5 | 215.9 | 221.1 | 215.9 | YES
47 | OK | 17 | 16 | 36 | 51 | 46.6 | 1.38 | 50 | 80.2 | 49.7 | 74.7 | 55 | 219.9 | 221.1 | 219.9 | YES
48 | OK | 31 | 39 | 39 | 39 | 54.8 | 0.69 | 50 | 80.2 | 49.7 | 77.5 | 52.4 | 216 | 221.1 | 216 | YES
49 | OK | 16 | 15 | 36 | 51 | 46.6 | 0.22 | 50 | 80.2 | 49.7 | 79.3 | 50.6 | 216.7 | 221.1 | 216.7 | YES
50 | OK | 39 | 49 | 49 | 39 | 93.1 | 0.62 | 50 | 80.2 | 49.7 | 77.7 | 52.1 | 216 | 221.1 | 216 | YES
| NG | 49 | 74 | 74 | 39 | 95.4 | 0.62 | 50 | 80.2 | 49.7 | 77.7 |  | 216 | 6.8353e+25 | 216 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 38-011645
TR_B (available) | 64-007498
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.2
TR_B Baseline Loading% | 49.7
Total Scenarios Evaluated | 51
Feasible Scenarios | 50
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 22
Tie Node (TR_A side) | 17
Tie Node (TR_B side) | 42
Tie Line Distance (m) | 1.4
Load Transferred (kW) | 6.27
TR_A Loading After (%) | 55.7
TR_B Loading After (%) | 62.4
Minimum Voltage (V) | 220.6