## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 13 | 14 | 26 | 12 | 2.6 | 12.97 | 50 | 80.7 | 35.6 | 29.1 | 45.5 | 215 | 214.3 | 214.3 | YES
| NG | 13 | 12 | 12 | 1 | 59.8 | 0.31 | 50 | 80.7 | 35.6 | 79.5 | 35.6 | 210 | 220.2 | 210 | NO
| NG | 13 | 4 | 4 | 12 | 45.5 | 7.1 | 50 | 80.7 | 35.6 | 52.8 | 66.3 | 209.7 | 189.2 | 189.2 | NO
2 | ** OPTIMAL ** | 14 | 6 | 26 | 12 | 2.6 | 12.73 | 50 | 80.7 | 35.6 | 30 | 44.5 | 214.8 | 215.1 | 214.8 | YES
| NG | 4 | 5 | 5 | 12 | 54.9 | 7.1 | 50 | 80.7 | 35.6 | 52.8 | 66.3 | 209.7 | 189.2 | 189.2 | NO
3 | OK | 6 | 7 | 26 | 12 | 2.6 | 12.59 | 50 | 80.7 | 35.6 | 30.6 | 43.9 | 214.7 | 215.6 | 214.7 | YES
| NG | 5 | 8 | 8 | 12 | 92.4 | 6.89 | 50 | 80.7 | 35.6 | 53.6 | 65.3 | 209.7 | 190.1 | 190.1 | NO
4 | OK | 7 | 30 | 26 | 12 | 2.6 | 12.59 | 50 | 80.7 | 35.6 | 30.6 | 43.9 | 214.7 | 215.6 | 214.7 | YES
| NG | 8 | 9 | 9 | 12 | 133.7 | 5.24 | 50 | 80.7 | 35.6 | 59.9 | 57.6 | 209.7 | 197.2 | 197.2 | NO
5 | OK | 30 | 29 | 26 | 12 | 2.6 | 6.16 | 50 | 80.7 | 35.6 | 56.1 | 43.9 | 214.7 | 215.6 | 214.7 | YES
6 | OK | 29 | 24 | 24 | 12 | 118.7 | 6.06 | 50 | 80.7 | 35.6 | 56.5 | 43.9 | 214.7 | 215.6 | 214.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-013139
TR_B (available) | 63-024454
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 35.6
Total Scenarios Evaluated | 11
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 6
Tie Node (TR_A side) | 26
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 2.6
Load Transferred (kW) | 12.73
TR_A Loading After (%) | 30
TR_B Loading After (%) | 44.5
Minimum Voltage (V) | 214.8