## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 14 | 37 | 9 | 100.3 | 12.97 | 50 | 80.7 | 6 | 29.1 | 68.5 | 215 | 161 | 161 | NO
| NG | 14 | 6 | 37 | 9 | 100.3 | 12.73 | 50 | 80.7 | 6 | 30 | 66.8 | 214.8 | 163.1 | 163.1 | NO
| NG | 6 | 7 | 37 | 9 | 100.3 | 12.59 | 50 | 80.7 | 6 | 30.6 | 65.8 | 214.7 | 164.2 | 164.2 | NO
| NG | 7 | 30 | 37 | 9 | 100.3 | 12.59 | 50 | 80.7 | 6 | 30.6 | 65.8 | 214.7 | 164.2 | 164.2 | NO
| NG | 30 | 31 | 37 | 9 | 100.3 | 6.43 | 50 | 80.7 | 6 | 54.6 | 32.1 | 213 | 209.5 | 209.5 | NO
1 | OK | 30 | 29 | 41 | 9 | 105.2 | 6.16 | 50 | 80.7 | 6 | 56.1 | 14.3 | 214.7 | 221.8 | 214.7 | YES
2 | OK | 31 | 44 | 37 | 9 | 100.3 | 5.54 | 50 | 80.7 | 6 | 58.1 | 28.2 | 213.1 | 213.2 | 213.1 | YES
3 | ** OPTIMAL ** | 29 | 24 | 41 | 9 | 105.2 | 6.06 | 50 | 80.7 | 6 | 56.5 | 14.3 | 214.7 | 221.8 | 214.7 | YES
4 | OK | 44 | 32 | 37 | 9 | 100.3 | 5.54 | 50 | 80.7 | 6 | 58.1 | 28.2 | 213.1 | 213.2 | 213.1 | YES
5 | OK | 24 | 19 | 41 | 9 | 105.2 | 3.68 | 50 | 80.7 | 6 | 65.7 | 7 | 213.3 | 229.1 | 213.3 | YES
6 | OK | 32 | 33 | 37 | 9 | 100.3 | 2.76 | 50 | 80.7 | 6 | 69.2 | 16.7 | 213.1 | 223 | 213.1 | YES
7 | OK | 19 | 20 | 41 | 9 | 105.2 | 3.68 | 50 | 80.7 | 6 | 65.7 | 7 | 213.3 | 229.1 | 213.3 | YES
8 | OK | 33 | 34 | 37 | 9 | 100.3 | 2.76 | 50 | 80.7 | 6 | 69.2 | 16.7 | 213.1 | 223 | 213.1 | YES
9 | OK | 20 | 43 | 41 | 9 | 105.2 | 3.68 | 50 | 80.7 | 6 | 65.7 | 7 | 213.3 | 229.1 | 213.3 | YES
10 | OK | 34 | 35 | 37 | 9 | 100.3 | 2.01 | 50 | 80.7 | 6 | 72.2 | 13.7 | 213.1 | 225.2 | 213.1 | YES
11 | OK | 43 | 42 | 41 | 9 | 105.2 | 1.12 | 50 | 80.7 | 6 | 76.1 | 7 | 210.9 | 229.1 | 210.9 | YES
12 | OK | 35 | 36 | 37 | 9 | 100.3 | 1.65 | 50 | 80.7 | 6 | 73.7 | 12.3 | 212.9 | 226.2 | 212.9 | YES
13 | OK | 42 | 16 | 41 | 9 | 105.2 | 0.8 | 50 | 80.7 | 6 | 77.3 | 6.4 | 210.7 | 229.5 | 210.7 | YES
14 | OK | 36 | 37 | 37 | 9 | 100.3 | 1 | 50 | 80.7 | 6 | 76.4 | 9.8 | 211.9 | 227.7 | 211.9 | YES
15 | OK | 16 | 18 | 41 | 9 | 105.2 | 0.8 | 50 | 80.7 | 6 | 77.3 | 6.4 | 210.7 | 229.5 | 210.7 | YES
16 | OK | 18 | 41 | 41 | 9 | 105.2 | 0.7 | 50 | 80.7 | 6 | 77.7 | 6 | 210.8 | 229.7 | 210.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-013139
TR_B (available) | 64-007006
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 6
Total Scenarios Evaluated | 21
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 24
Tie Node (TR_A side) | 41
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 105.2
Load Transferred (kW) | 6.06
TR_A Loading After (%) | 56.5
TR_B Loading After (%) | 14.3
Minimum Voltage (V) | 214.7