## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 54 | 46 | 35 | 38 | 143 | 24.64 | 50 | 46.5 | 46.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 54 | 58 | 61 | 38 | 143.4 | 1.54 | 50 | 46.5 | 46.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 46 | 45 | 39 | 40 | 198 | 20.09 | 50 | 46.5 | 46.2 | 16 | 56.8 | 226.5 | 194.8 | 194.8 | NO
1 | OK | 46 | 30 | 35 | 38 | 143 | 4.55 | 50 | 46.5 | 46.2 | 30.4 | 49.9 | 222.3 | 213.7 | 213.7 | YES
2 | ** OPTIMAL ** | 58 | 59 | 61 | 38 | 143.4 | 1.22 | 50 | 46.5 | 46.2 | 41.8 | 46.2 | 220 | 223 | 220 | YES
| NG | 45 | 53 | 39 | 40 | 198 | 19.27 | 50 | 46.5 | 46.2 | 19.1 | 55.5 | 225.9 | 198.7 | 198.7 | NO
3 | OK | 30 | 31 | 35 | 38 | 143 | 2.96 | 50 | 46.5 | 46.2 | 30.4 | 49.9 | 222.3 | 213.7 | 213.7 | YES
4 | OK | 59 | 60 | 61 | 38 | 143.4 | 0.98 | 50 | 46.5 | 46.2 | 42.7 | 46.2 | 219.9 | 223 | 219.9 | YES
| NG | 53 | 41 | 39 | 40 | 198 | 19.27 | 50 | 46.5 | 46.2 | 19.1 | 55.5 | 225.9 | 198.7 | 198.7 | NO
5 | OK | 31 | 32 | 35 | 38 | 143 | 2.59 | 50 | 46.5 | 46.2 | 32.8 | 49.4 | 221.8 | 214.9 | 214.9 | YES
6 | OK | 60 | 61 | 61 | 38 | 143.4 | 0.38 | 50 | 46.5 | 46.2 | 45 | 46.2 | 219.4 | 223 | 219.4 | YES
| NG | 41 | 40 | 39 | 40 | 198 | 17.65 | 50 | 46.5 | 46.2 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
7 | OK | 32 | 33 | 35 | 38 | 143 | 2.59 | 50 | 46.5 | 46.2 | 32.8 | 49.4 | 221.8 | 214.9 | 214.9 | YES
| NG | 40 | 65 | 39 | 40 | 198 | 17.65 | 50 | 46.5 | 46.2 | [5 empty] | NO | TR_A sim: not converged
8 | OK | 65 | 43 | 39 | 40 | 198 | 8.27 | 50 | 46.5 | 46.2 | 28.1 | 51.6 | 224.2 | 211.2 | 211.2 | YES
9 | OK | 43 | 42 | 39 | 40 | 198 | 8.27 | 50 | 46.5 | 46.2 | 28.1 | 51.6 | 224.2 | 211.2 | 211.2 | YES
10 | OK | 42 | 12 | 39 | 40 | 198 | 8.08 | 50 | 46.5 | 46.2 | 28.9 | 51.3 | 224 | 211.9 | 211.9 | YES
11 | OK | 12 | 1 | 39 | 40 | 198 | 8.08 | 50 | 46.5 | 46.2 | 28.9 | 51.3 | 224 | 211.9 | 211.9 | YES
12 | OK | 1 | 0 | 39 | 40 | 198 | 7.99 | 50 | 46.5 | 46.2 | 30.9 | 50.6 | 223.6 | 214 | 214 | YES
13 | OK | 0 | 17 | 39 | 40 | 198 | 4.58 | 50 | 46.5 | 46.2 | 32.6 | 50.6 | 223.3 | 214 | 214 | YES
14 | OK | 17 | 36 | 39 | 40 | 198 | 2.69 | 50 | 46.5 | 46.2 | 36 | 49.5 | 222.6 | 217.2 | 217.2 | YES
15 | OK | 36 | 18 | 39 | 40 | 198 | 2.3 | 50 | 46.5 | 46.2 | 36 | 49 | 222.6 | 218.6 | 218.6 | YES
16 | OK | 18 | 19 | 39 | 40 | 198 | 1.88 | 50 | 46.5 | 46.2 | 39.1 | 48.5 | 222 | 219.9 | 219.9 | YES
17 | OK | 19 | 20 | 39 | 40 | 198 | 0.24 | 50 | 46.5 | 46.2 | 45.5 | 46.5 | 219.5 | 222.9 | 219.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-017026
TR_B (available) | 29-000113
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 46.5
TR_B Baseline Loading% | 46.2
Total Scenarios Evaluated | 24
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 58
Switch Child Node | 59
Tie Node (TR_A side) | 61
Tie Node (TR_B side) | 38
Tie Line Distance (m) | 143.4
Load Transferred (kW) | 1.22
TR_A Loading After (%) | 41.8
TR_B Loading After (%) | 46.2
Minimum Voltage (V) | 220