## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 54 | 58 | 58 | 13 | 54.8 | 1.54 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 46 | 45 | 4 | 15 | 2.2 | 20.09 | 50 | 46.5 | 13 | 16 | 43.9 | 226.5 | 216.1 | 216.1 | YES
2 | OK | 46 | 30 | 30 | 13 | 61.2 | 4.55 | 50 | 46.5 | 13 | 30.4 | 24.4 | 222.3 | 223.5 | 222.3 | YES
3 | OK | 58 | 59 | 59 | 13 | 78 | 1.22 | 50 | 46.5 | 13 | 41.8 | 13 | 220 | 227.5 | 220 | YES
4 | OK | 45 | 11 | 10 | 13 | 15.8 | 0.82 | 50 | 46.5 | 13 | 43.4 | 16.1 | 219.5 | 226.9 | 219.5 | YES
5 | OK | 45 | 53 | 4 | 15 | 2.2 | 19.27 | 50 | 46.5 | 13 | 19.1 | 40.6 | 225.9 | 217.3 | 217.3 | YES
6 | OK | 30 | 31 | 31 | 13 | 77.2 | 2.96 | 50 | 46.5 | 13 | 30.4 | 24.4 | 222.3 | 223.6 | 222.3 | YES
7 | OK | 53 | 41 | 4 | 15 | 2.2 | 19.27 | 50 | 46.5 | 13 | 19.1 | 40.6 | 225.9 | 217.3 | 217.3 | YES
8 | OK | 31 | 32 | 32 | 13 | 106.8 | 2.59 | 50 | 46.5 | 13 | 32.8 | 23 | 221.8 | 224.2 | 221.8 | YES
| NG | 41 | 40 | 4 | 15 | 2.2 | 17.65 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
| NG | 41 | 56 | 56 | 13 | 8.3 | 1.62 | 50 | 46.5 | 13 | 44.7 |  | 219.8 | 5.0808e+58 | 219.8 | NO
9 | OK | 32 | 33 | 33 | 13 | 108.9 | 2.59 | 50 | 46.5 | 13 | 32.8 | 23 | 221.8 | 224.2 | 221.8 | YES
| NG | 40 | 65 | 4 | 15 | 2.2 | 17.65 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: not converged
10 | OK | 56 | 57 | 52 | 16 | 21.9 | 0.44 | 50 | 46.5 | 13 | 44.8 | 13 | 219.6 | 227.5 | 219.6 | YES
| NG | 56 | 47 | 47 | 13 | 10.4 | 1.18 | 50 | 46.5 | 13 | [5 empty] | NO | TR_B sim: not converged
11 | OK | 65 | 9 | 4 | 15 | 2.2 | 6.03 | 50 | 46.5 | 13 | 41.9 | 17.5 | 220.1 | 226.7 | 220.1 | YES
| NG | 65 | 44 | 44 | 13 | 10.5 | 3.35 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: not converged
12 | OK | 65 | 43 | 43 | 13 | 6.5 | 8.27 | 50 | 46.5 | 13 | 28.1 | 29.7 | 224.2 | 221.2 | 221.2 | YES
| NG | 47 | 48 | 48 | 13 | 32 | 1.18 | 50 | 46.5 | 13 | 46.5 |  | 219.1 | 6.1243e+25 | 219.1 | NO
13 | OK | 9 | 8 | 4 | 15 | 2.2 | 6.03 | 50 | 46.5 | 13 | 41.9 | 17.5 | 220.1 | 226.7 | 220.1 | YES
| NG | 44 | 21 | 21 | 13 | 32.9 | 3.35 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
14 | OK | 43 | 42 | 42 | 13 | 8.5 | 8.27 | 50 | 46.5 | 13 | 28.1 | 29.7 | 224.2 | 221.2 | 221.2 | YES
| NG | 48 | 49 | 50 | 12 | 40.8 | 0.7 | 50 | 46.5 | 13 | [5 empty] | NO | TR_B sim: not converged
15 | OK | 8 | 7 | 4 | 15 | 2.2 | 3.74 | 50 | 46.5 | 13 | 41.9 | 17.5 | 220.1 | 226.7 | 220.1 | YES
| NG | 21 | 2 | 25 | 12 | 38.5 | 3.02 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: not converged
16 | OK | 42 | 12 | 12 | 13 | 13.5 | 8.08 | 50 | 46.5 | 13 | 28.9 | 29 | 224 | 221.4 | 221.4 | YES
17 | OK | 49 | 50 | 50 | 12 | 40.8 | 0.41 | 50 | 46.5 | 13 | 46.5 | 13 | 219.1 | 227.5 | 219.1 | YES
| NG | 49 | 62 | 62 | 13 | 60.1 | 0.29 | 50 | 46.5 | 13 | [5 empty] | NO | TR_B sim: not converged
18 | OK | 7 | 6 | 4 | 15 | 2.2 | 3.39 | 50 | 46.5 | 13 | 41.9 | 17.5 | 220.1 | 226.7 | 220.1 | YES
| NG | 2 | 3 | 3 | 13 | 57.6 | 1.41 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: not converged
19 | OK | 2 | 23 | 25 | 12 | 38.5 | 1.61 | 50 | 46.5 | 13 | 46.5 | 19.1 | 219.1 | 226.4 | 219.1 | YES
20 | OK | 12 | 1 | 67 | 16 | 19.9 | 8.08 | 50 | 46.5 | 13 | 28.9 | 44.6 | 224 | 215.5 | 215.5 | YES
| NG | 62 | 63 | 63 | 13 | 88.8 | 0.29 | 50 | 46.5 | 13 | 46.5 |  | 219.1 | 5.0808e+58 | 219.1 | NO
21 | OK | 6 | 5 | 4 | 15 | 2.2 | 2.82 | 50 | 46.5 | 13 | 41.9 | 17.5 | 220.1 | 226.7 | 220.1 | YES
| NG | 3 | 22 | 22 | 13 | 68.4 | 1.41 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
22 | OK | 23 | 24 | 25 | 12 | 38.5 | 1.1 | 50 | 46.5 | 13 | 46.5 | 17.2 | 219.1 | 226.7 | 219.1 | YES
23 | OK | 1 | 0 | 67 | 16 | 19.9 | 7.99 | 50 | 46.5 | 13 | 30.9 | 42.4 | 223.6 | 216.4 | 216.4 | YES
| NG | 63 | 64 | 64 | 13 | 119.4 | 0.23 | 50 | 46.5 | 13 | 46.5 |  | 219.1 | 5.0808e+58 | 219.1 | NO
24 | OK | 5 | 4 | 4 | 15 | 2.2 | 1.3 | 50 | 46.5 | 13 | 45.2 | 14.2 | 219.4 | 227.3 | 219.4 | YES
| NG | 22 | 26 | 26 | 13 | 77.1 | 1.11 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
25 | OK | 24 | 25 | 25 | 12 | 38.5 | 0.22 | 50 | 46.5 | 13 | 46.5 | 13 | 219.1 | 227.5 | 219.1 | YES
26 | OK | 0 | 17 | 17 | 13 | 82.5 | 4.58 | 50 | 46.5 | 13 | 32.6 | 26.8 | 223.3 | 222.3 | 222.3 | YES
27 | OK | 0 | 13 | 67 | 16 | 19.9 | 2.95 | 50 | 46.5 | 13 | 46.5 | 24.3 | 219.1 | 224.9 | 219.1 | YES
28 | OK | 4 | 37 | 37 | 15 | 2.6 | 0.8 | 50 | 46.5 | 13 | 46.5 | 13 | 219.1 | 227.5 | 219.1 | YES
| NG | 26 | 28 | 28 | 13 | 91.3 | 0.27 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
29 | OK | 26 | 27 | 27 | 13 | 89.9 | 0.84 | 50 | 46.5 | 13 | 43.2 | 16.2 | 219.8 | 226.9 | 219.8 | YES
30 | OK | 17 | 36 | 36 | 13 | 112.7 | 2.69 | 50 | 46.5 | 13 | 36 | 23.4 | 222.6 | 223.7 | 222.6 | YES
31 | OK | 13 | 14 | 67 | 16 | 19.9 | 1.82 | 50 | 46.5 | 13 | 46.5 | 19.9 | 219.1 | 226.2 | 219.1 | YES
| NG | 28 | 29 | 29 | 13 | 118.1 | 0.03 | 50 | 46.5 | 13 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
32 | ** OPTIMAL ** | 36 | 18 | 18 | 13 | 117.2 | 2.3 | 50 | 46.5 | 13 | 36 | 21.8 | 222.6 | 224.4 | 222.6 | YES
33 | OK | 14 | 15 | 67 | 16 | 19.9 | 1.04 | 50 | 46.5 | 13 | 46.5 | 17 | 219.1 | 226.8 | 219.1 | YES
34 | OK | 15 | 16 | 67 | 16 | 19.9 | 0.16 | 50 | 46.5 | 13 | 46.5 | 13.6 | 219.1 | 227.4 | 219.1 | YES
35 | OK | 16 | 66 | 67 | 16 | 19.9 | 0.16 | 50 | 46.5 | 13 | 46.5 | 13.6 | 219.1 | 227.4 | 219.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-017026
TR_B (available) | 38-017025
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 46.5
TR_B Baseline Loading% | 13
Total Scenarios Evaluated | 53
Feasible Scenarios | 35
--- Optimal Solution ---
Switch Parent Node | 36
Switch Child Node | 18
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 117.2
Load Transferred (kW) | 2.3
TR_A Loading After (%) | 36
TR_B Loading After (%) | 21.8
Minimum Voltage (V) | 222.6