## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 39 | 38 | 57 | 29 | 5.2 | 13.82 | 50 | 86.4 | 28.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 39 | 40 | 40 | 29 | 101.8 | 8.55 | 50 | 86.4 | 28.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 38 | 52 | 57 | 29 | 5.2 | 13.31 | 50 | 86.4 | 28.7 | 34.8 | 57.8 | 221.8 | 211.2 | 211.2 | YES
2 | OK | 40 | 49 | 49 | 29 | 104.2 | 7.83 | 50 | 86.4 | 28.7 | 53.8 | 45.6 | 219.9 | 212.2 | 212.2 | YES
3 | OK | 52 | 32 | 57 | 29 | 5.2 | 12.93 | 50 | 86.4 | 28.7 | 35.8 | 56.8 | 221.6 | 211.6 | 211.6 | YES
4 | OK | 49 | 41 | 41 | 29 | 143.3 | 7.27 | 50 | 86.4 | 28.7 | 58.4 | 43.3 | 219 | 213.4 | 213.4 | YES
5 | OK | 32 | 16 | 57 | 29 | 5.2 | 12.93 | 50 | 86.4 | 28.7 | 36.2 | 56.8 | 221.6 | 211.6 | 211.6 | YES
6 | OK | 41 | 28 | 29 | 29 | 145.4 | 6.57 | 50 | 86.4 | 28.7 | 61.1 | 43.3 | 219 | 214.7 | 214.7 | YES
7 | OK | 16 | 15 | 15 | 29 | 59.9 | 2.24 | 50 | 86.4 | 28.7 | 77.7 | 35.8 | 217.6 | 219.4 | 217.6 | YES
8 | OK | 16 | 1 | 57 | 29 | 5.2 | 10.69 | 50 | 86.4 | 28.7 | 44.8 | 49.4 | 220.2 | 214.5 | 214.5 | YES
9 | OK | 28 | 37 | 37 | 29 | 183.3 | 5.08 | 50 | 86.4 | 28.7 | 66.8 | 40.5 | 218.5 | 215 | 215 | YES
10 | OK | 1 | 0 | 57 | 29 | 5.2 | 10.69 | 50 | 86.4 | 28.7 | 44.8 | 49.4 | 220.2 | 214.5 | 214.5 | YES
11 | OK | 37 | 44 | 44 | 29 | 217.1 | 4.24 | 50 | 86.4 | 28.7 | 70 | 40.5 | 218.5 | 215 | 215 | YES
12 | OK | 0 | 57 | 57 | 29 | 5.2 | 10.69 | 50 | 86.4 | 28.7 | 44.8 | 49.4 | 220.2 | 214.5 | 214.5 | YES
13 | OK | 44 | 45 | 45 | 29 | 219.1 | 4.24 | 50 | 86.4 | 28.7 | 70 | 40.5 | 218.5 | 215 | 215 | YES
14 | OK | 57 | 20 | 20 | 29 | 15.8 | 10.69 | 50 | 86.4 | 28.7 | 44.8 | 49.4 | 220.2 | 214.6 | 214.6 | YES
15 | OK | 45 | 30 | 30 | 29 | 224.7 | 4.24 | 50 | 86.4 | 28.7 | 70 | 40.5 | 218.5 | 215 | 215 | YES
16 | OK | 20 | 19 | 19 | 29 | 51.3 | 9.46 | 50 | 86.4 | 28.7 | 49.5 | 49.4 | 220.2 | 214.6 | 214.6 | YES
17 | OK | 19 | 5 | 5 | 29 | 57.6 | 8.98 | 50 | 86.4 | 28.7 | 51.4 | 48.1 | 220 | 215.2 | 215.2 | YES
18 | OK | 5 | 4 | 4 | 29 | 90.4 | 8.71 | 50 | 86.4 | 28.7 | 52.4 | 47.6 | 219.9 | 215.4 | 215.4 | YES
19 | OK | 4 | 21 | 21 | 29 | 97.4 | 6.39 | 50 | 86.4 | 28.7 | 61.4 | 38.3 | 218.1 | 218.9 | 218.1 | YES
20 | OK | 4 | 61 | 61 | 29 | 97.1 | 2.32 | 50 | 86.4 | 28.7 | 77.3 | 37.6 | 218 | 219 | 218 | YES
21 | ** OPTIMAL ** | 21 | 8 | 8 | 29 | 132.5 | 6.23 | 50 | 86.4 | 28.7 | 62 | 38.3 | 218.1 | 218.9 | 218.1 | YES
22 | OK | 61 | 60 | 60 | 29 | 115.3 | 2.08 | 50 | 86.4 | 28.7 | 78.2 | 36.7 | 217.8 | 219.2 | 217.8 | YES
23 | OK | 8 | 7 | 7 | 29 | 168.6 | 4.85 | 50 | 86.4 | 28.7 | 67.4 | 34.6 | 217.4 | 219.6 | 217.4 | YES
24 | OK | 60 | 27 | 27 | 29 | 136.8 | 1.99 | 50 | 86.4 | 28.7 | 78.6 | 36.3 | 217.7 | 219.3 | 217.7 | YES
25 | OK | 7 | 6 | 33 | 29 | 171.3 | 3.48 | 50 | 86.4 | 28.7 | 72.7 | 28.7 | 217 | 220.8 | 217 | YES
26 | OK | 6 | 22 | 22 | 18 | 220.7 | 2.25 | 50 | 86.4 | 28.7 | 77.5 | 32.8 | 217 | 220 | 217 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-017084
TR_B (available) | 60-008310
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 86.4
TR_B Baseline Loading% | 28.7
Total Scenarios Evaluated | 28
Feasible Scenarios | 26
--- Optimal Solution ---
Switch Parent Node | 21
Switch Child Node | 8
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 132.5
Load Transferred (kW) | 6.23
TR_A Loading After (%) | 62
TR_B Loading After (%) | 38.3
Minimum Voltage (V) | 218.1