## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 32 | 33 | 5 | 1 | 11.6 | 12.84 | 50 | 87.2 | 2.4 | 36.6 | 39.4 | 219 | 187.3 | 187.3 | NO
| NG | 33 | 17 | 5 | 1 | 11.6 | 12.33 | 50 | 87.2 | 2.4 | 38.6 | 36.9 | 218.7 | 190.8 | 190.8 | NO
| NG | 17 | 16 | 5 | 1 | 11.6 | 12.16 | 50 | 87.2 | 2.4 | 39.2 | 36.9 | 218.7 | 190.8 | 190.8 | NO
| NG | 16 | 15 | 5 | 1 | 11.6 | 11.23 | 50 | 87.2 | 2.4 | 42.8 | 33.6 | 218.3 | 195.3 | 195.3 | NO
| NG | 15 | 13 | 5 | 1 | 11.6 | 10.6 | 50 | 87.2 | 2.4 | 45.2 | 33.6 | 218.3 | 195.3 | 195.3 | NO
| NG | 13 | 14 | 5 | 1 | 11.6 | 9.19 | 50 | 87.2 | 2.4 | 50.6 | 26.7 | 217.2 | 204.6 | 204.6 | NO
| NG | 14 | 48 | 5 | 1 | 11.6 | 8.82 | 50 | 87.2 | 2.4 | 52 | 25 | 216.9 | 206.8 | 206.8 | NO
| NG | 48 | 12 | 5 | 1 | 11.6 | 6.49 | 50 | 87.2 | 2.4 | 61 | 25 | 216.9 | 206.8 | 206.8 | NO
| NG | 12 | 11 | 5 | 1 | 11.6 | 6.08 | 50 | 87.2 | 2.4 | 62.6 | 24.3 | 216.8 | 207.6 | 207.6 | NO
| NG | 11 | 9 | 5 | 1 | 11.6 | 5.53 | 50 | 87.2 | 2.4 | 64.7 | 24.3 | 216.8 | 207.6 | 207.6 | NO
1 | OK | 9 | 10 | 5 | 1 | 11.6 | 4.27 | 50 | 87.2 | 2.4 | 69.6 | 18.7 | 215.8 | 214.3 | 214.3 | YES
2 | ** OPTIMAL ** | 10 | 41 | 5 | 1 | 11.6 | 3.83 | 50 | 87.2 | 2.4 | 69.8 | 16.8 | 215.8 | 216.5 | 215.8 | YES
3 | OK | 41 | 8 | 5 | 1 | 11.6 | 3.83 | 50 | 87.2 | 2.4 | 71.4 | 16.8 | 215.5 | 216.5 | 215.5 | YES
4 | OK | 8 | 6 | 5 | 1 | 11.6 | 3.58 | 50 | 87.2 | 2.4 | 72.4 | 16.8 | 215.5 | 216.5 | 215.5 | YES
5 | OK | 6 | 7 | 5 | 1 | 11.6 | 2.81 | 50 | 87.2 | 2.4 | 75.4 | 13.6 | 214.9 | 219.2 | 214.9 | YES
6 | OK | 7 | 35 | 5 | 1 | 11.6 | 2.81 | 50 | 87.2 | 2.4 | 75.4 | 13.6 | 214.9 | 219.2 | 214.9 | YES
7 | OK | 35 | 5 | 5 | 1 | 11.6 | 2.67 | 50 | 87.2 | 2.4 | 76 | 13 | 214.8 | 219.7 | 214.8 | YES
8 | OK | 5 | 4 | 4 | 1 | 41.1 | 2.67 | 50 | 87.2 | 2.4 | 76 | 13 | 214.8 | 219.9 | 214.8 | YES
9 | OK | 4 | 39 | 39 | 1 | 47.8 | 2.44 | 50 | 87.2 | 2.4 | 76.8 | 12 | 214.6 | 220.7 | 214.6 | YES
10 | OK | 39 | 3 | 3 | 1 | 80.9 | 2.44 | 50 | 87.2 | 2.4 | 76.9 | 12 | 214.6 | 220.7 | 214.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 38-018013
TR_B (available) | 61-003737
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 87.2
TR_B Baseline Loading% | 2.4
Total Scenarios Evaluated | 20
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 41
Tie Node (TR_A side) | 5
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 11.6
Load Transferred (kW) | 3.83
TR_A Loading After (%) | 69.8
TR_B Loading After (%) | 16.8
Minimum Voltage (V) | 215.8