## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 10 | 11 | 49 | 8 | 29.6 | 3.65 | 50 | 81.2 | 17.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 10 | 15 | 13 | 20 | 2.9 | 17.38 | 50 | 81.2 | 17.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 11 | 12 | 49 | 8 | 29.6 | 3.24 | 50 | 81.2 | 17.5 | 68.8 | 29.9 | 219.6 | 225.4 | 219.6 | YES
2 | OK | 15 | 13 | 13 | 20 | 2.9 | 15.11 | 50 | 81.2 | 17.5 | 22.6 | 76.1 | 228 | 218.3 | 218.3 | YES
3 | OK | 12 | 17 | 49 | 8 | 29.6 | 2.1 | 50 | 81.2 | 17.5 | 73.1 | 25.5 | 219 | 225.6 | 219 | YES
4 | OK | 12 | 61 | 61 | 20 | 105.8 | 1.14 | 50 | 81.2 | 17.5 | 76.8 | 21.9 | 218.9 | 226.2 | 218.9 | YES
5 | OK | 13 | 14 | 40 | 5 | 22.7 | 15.11 | 50 | 81.2 | 17.5 | 22.6 | 76.5 | 228 | 216.6 | 216.6 | YES
6 | OK | 17 | 16 | 49 | 8 | 29.6 | 1.5 | 50 | 81.2 | 17.5 | 75.4 | 23.2 | 219 | 226 | 219 | YES
7 | OK | 61 | 8 | 7 | 19 | 144.9 | 0.62 | 50 | 81.2 | 17.5 | 78.8 | 19.9 | 218.6 | 226.3 | 218.6 | YES
8 | ** OPTIMAL ** | 14 | 40 | 40 | 5 | 22.7 | 6.53 | 50 | 81.2 | 17.5 | 55.7 | 42.8 | 221.5 | 222.5 | 221.5 | YES
9 | OK | 14 | 45 | 45 | 17 | 24.2 | 2.47 | 50 | 81.2 | 17.5 | 70.5 | 27 | 220 | 225.5 | 220 | YES
10 | OK | 14 | 34 | 34 | 17 | 30.6 | 5.84 | 50 | 81.2 | 17.5 | 58.4 | 40 | 221.1 | 223.3 | 221.1 | YES
11 | OK | 16 | 5 | 49 | 8 | 29.6 | 0.97 | 50 | 81.2 | 17.5 | 77.4 | 21.2 | 218.7 | 226.2 | 218.7 | YES
12 | OK | 8 | 7 | 7 | 19 | 144.9 | 0.62 | 50 | 81.2 | 17.5 | 78.8 | 19.9 | 218.6 | 226.3 | 218.6 | YES
13 | OK | 40 | 43 | 43 | 4 | 22.8 | 5.27 | 50 | 81.2 | 17.5 | 60.5 | 38 | 221.5 | 223.6 | 221.5 | YES
14 | OK | 45 | 33 | 33 | 20 | 47 | 2.47 | 50 | 81.2 | 17.5 | 71.6 | 27 | 219.7 | 225.6 | 219.7 | YES
15 | OK | 34 | 35 | 35 | 17 | 56.8 | 5.84 | 50 | 81.2 | 17.5 | 58.4 | 40 | 221.1 | 223.3 | 221.1 | YES
16 | OK | 5 | 4 | 49 | 8 | 29.6 | 0.97 | 50 | 81.2 | 17.5 | 77.4 | 21.2 | 218.7 | 226.2 | 218.7 | YES
17 | OK | 43 | 31 | 31 | 0 | 22.8 | 5.1 | 50 | 81.2 | 17.5 | 61.2 | 37.3 | 221.4 | 223.4 | 221.4 | YES
18 | OK | 33 | 0 | 0 | 20 | 70 | 2.14 | 50 | 81.2 | 17.5 | 72.8 | 25.7 | 219.6 | 225.7 | 219.6 | YES
19 | OK | 35 | 44 | 44 | 17 | 119.1 | 5.59 | 50 | 81.2 | 17.5 | 59.3 | 39.1 | 221.1 | 223.6 | 221.1 | YES
20 | OK | 4 | 3 | 3 | 8 | 106.9 | 0.85 | 50 | 81.2 | 17.5 | 77.9 | 20.7 | 218.6 | 226.2 | 218.6 | YES
21 | OK | 31 | 32 | 32 | 0 | 63 | 4.98 | 50 | 81.2 | 17.5 | 61.6 | 36.9 | 221.4 | 223.6 | 221.4 | YES
22 | OK | 0 | 1 | 1 | 20 | 101 | 0.89 | 50 | 81.2 | 17.5 | 77.7 | 20.9 | 218.9 | 226.2 | 218.9 | YES
23 | OK | 0 | 30 | 30 | 20 | 108.2 | 1.25 | 50 | 81.2 | 17.5 | 76.3 | 22.3 | 219 | 226 | 219 | YES
24 | OK | 32 | 41 | 41 | 6 | 105.9 | 4.33 | 50 | 81.2 | 17.5 | 64.2 | 34.3 | 220.7 | 223.6 | 220.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 40-016303
TR_B (available) | 57-006835
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.2
TR_B Baseline Loading% | 17.5
Total Scenarios Evaluated | 26
Feasible Scenarios | 24
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 40
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 22.7
Load Transferred (kW) | 6.53
TR_A Loading After (%) | 55.7
TR_B Loading After (%) | 42.8
Minimum Voltage (V) | 221.5