## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 33 | 34 | 47 | 4 | 1.8 | 7.59 | 50 | 83 | 37.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 34 | 3 | 47 | 4 | 1.8 | 7.23 | 50 | 83 | 37.6 | 54.9 | 66.1 | 210.8 | 209.6 | 209.6 | NO
1 | ** OPTIMAL ** | 3 | 2 | 2 | 4 | 205.2 | 6.79 | 50 | 83 | 37.6 | 56.6 | 64.4 | 210.5 | 210.3 | 210.3 | YES
| NG | 27 | 15 | 17 | 0 | 164.1 | 10.9 | 50 | 83 | 37.6 | 39.8 | 84.9 | 218.7 | 185.8 | 185.8 | NO
| NG | 15 | 45 | 17 | 0 | 164.1 | 1.25 | 50 | 83 | 37.6 | 78 | 42.4 | 206.3 | 219.4 | 206.3 | NO
| NG | 45 | 50 | 17 | 0 | 164.1 | 1.25 | 50 | 83 | 37.6 | 78 | 42.4 | 206.3 | 219.4 | 206.3 | NO
| NG | 50 | 39 | 17 | 0 | 164.1 | 1.03 | 50 | 83 | 37.6 | 78.9 | 41.6 | 206 | 219.6 | 206 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 40-016411
TR_B (available) | 64-006094
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83
TR_B Baseline Loading% | 37.6
Total Scenarios Evaluated | 7
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 2
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 205.2
Load Transferred (kW) | 6.79
TR_A Loading After (%) | 56.6
TR_B Loading After (%) | 64.4
Minimum Voltage (V) | 210.3