## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 29 | 1 | 76 | 9 | 20.5 | 59.06 | 50 | 68.3 | 14.6 | 23.5 | 62.3 | 225 | 186.5 | 186.5 | NO
| NG | 29 | 32 | 126 | 12 | 33.6 | 11.56 | 95 | 68.3 | 14.6 | 60 | 22.9 | 200 | 218.6 | 200 | NO
| NG | 1 | 0 | 76 | 9 | 20.5 | 57.66 | 50 | 68.3 | 14.6 | 24.7 | 61.1 | 224.8 | 185.5 | 185.5 | NO
| NG | 32 | 34 | 7 | 12 | 94.1 | 2.24 | 95 | 68.3 | 14.6 | 66.7 | 16.2 | 199.6 | 218.9 | 199.6 | NO
| NG | 32 | 126 | 126 | 12 | 33.6 | 5.69 | 95 | 68.3 | 14.6 | 64.2 | 18.7 | 199.7 | 218.8 | 199.7 | NO
| NG | 0 | 66 | 76 | 9 | 20.5 | 54.06 | 50 | 68.3 | 14.6 | 27.3 | 57.7 | 224.8 | 191.4 | 191.4 | NO
| NG | 34 | 36 | 7 | 12 | 94.1 | 1.69 | 95 | 68.3 | 14.6 | 67.1 | 15.8 | 199.6 | 218.9 | 199.6 | NO
| NG | 126 | 132 | 132 | 12 | 37.2 | 5.69 | 95 | 68.3 | 14.6 | 64.2 | 18.7 | 199.7 | 218.8 | 199.7 | NO
| NG | 66 | 67 | 76 | 9 | 20.5 | 51.09 | 50 | 68.3 | 14.6 | 29.4 | 54.8 | 224.7 | 195.2 | 195.2 | NO
| NG | 36 | 35 | 7 | 12 | 94.1 | 0.63 | 95 | 68.3 | 14.6 | 67.8 | 15 | 199.5 | 218.9 | 199.5 | NO
| NG | 132 | 91 | 91 | 12 | 53.6 | 5.04 | 95 | 68.3 | 14.6 | 64.6 | 18.2 | 199.7 | 218.9 | 199.7 | NO
| NG | 67 | 70 | 76 | 9 | 20.5 | 46.77 | 50 | 68.3 | 14.6 | 32.5 | 51 | 224.5 | 198.5 | 198.5 | NO
| NG | 35 | 93 | 7 | 12 | 94.1 | 0.2 | 95 | 68.3 | 14.6 | 68.1 | 14.7 | 199.5 | 219 | 199.5 | NO
| NG | 91 | 90 | 90 | 12 | 75.1 | 4.74 | 95 | 68.3 | 14.6 | 64.8 | 18 | 199.7 | 218.9 | 199.7 | NO
| NG | 70 | 104 | 76 | 9 | 20.5 | 46.59 | 50 | 68.3 | 14.6 | 32.5 | 50.8 | 224.5 | 198.9 | 198.9 | NO
| NG | 93 | 7 | 7 | 12 | 94.1 | 0.2 | 95 | 68.3 | 14.6 | 68.1 | 14.7 | 199.5 | 219 | 199.5 | NO
| NG | 90 | 6 | 6 | 12 | 80.8 | 2.77 | 95 | 68.3 | 14.6 | 66.3 | 15.6 | 199.6 | 219 | 199.6 | NO
| NG | 104 | 86 | 76 | 9 | 20.5 | 46.44 | 50 | 68.3 | 14.6 | 32.8 | 48.9 | 224.5 | 198.5 | 198.5 | NO
| NG | 86 | 87 | 76 | 9 | 20.5 | 44.41 | 50 | 68.3 | 14.6 | 34.2 | 48.9 | 224.5 | 198.5 | 198.5 | NO
| NG | 87 | 77 | 76 | 9 | 20.5 | 44.02 | 50 | 68.3 | 14.6 | 34.5 | 48.6 | 224.5 | 198.4 | 198.4 | NO
| NG | 77 | 78 | 65 | 12 | 138.9 | 23.99 | 50 | 68.3 | 14.6 | 49.8 | 28.4 | 204.6 | 212.4 | 204.6 | NO
1 | ** OPTIMAL ** | 77 | 71 | 76 | 9 | 20.5 | 20.03 | 50 | 68.3 | 14.6 | 52.4 | 29.4 | 214.3 | 216.6 | 214.3 | YES
| NG | 78 | 92 | 65 | 12 | 138.9 | 22.97 | 50 | 68.3 | 14.6 | 50.5 | 28.4 | 204.6 | 212.4 | 204.6 | NO
2 | OK | 71 | 72 | 76 | 9 | 20.5 | 18.21 | 50 | 68.3 | 14.6 | 53.7 | 28 | 213.4 | 216.8 | 213.4 | YES
| NG | 92 | 79 | 65 | 12 | 138.9 | 21.38 | 50 | 68.3 | 14.6 | 51.8 | 27.1 | 203.4 | 212.2 | 203.4 | NO
3 | OK | 72 | 73 | 76 | 9 | 20.5 | 17.34 | 50 | 68.3 | 14.6 | 54.4 | 27.4 | 213 | 216.7 | 213 | YES
| NG | 79 | 55 | 65 | 12 | 138.9 | 21.38 | 50 | 68.3 | 14.6 | 51.8 | 27.1 | 203.4 | 212.2 | 203.4 | NO
4 | OK | 73 | 74 | 76 | 9 | 20.5 | 16.5 | 50 | 68.3 | 14.6 | 55 | 26.8 | 212.7 | 216.7 | 212.7 | YES
| NG | 55 | 131 | 65 | 12 | 138.9 | 9.19 | 50 | 68.3 | 14.6 | 61 | 21.4 | 200.9 | 218.1 | 200.9 | NO
5 | OK | 74 | 75 | 76 | 9 | 20.5 | 14.98 | 50 | 68.3 | 14.6 | 56.2 | 25.6 | 212.7 | 218.1 | 212.7 | YES
| NG | 131 | 58 | 65 | 12 | 138.9 | 9.15 | 50 | 68.3 | 14.6 | 61 | 21.3 | 200.9 | 218.1 | 200.9 | NO
6 | OK | 75 | 108 | 76 | 9 | 20.5 | 13.28 | 50 | 68.3 | 14.6 | 57.5 | 24.4 | 212.1 | 218.6 | 212.1 | YES
| NG | 58 | 57 | 65 | 12 | 138.9 | 8.33 | 50 | 68.3 | 14.6 | 61.7 | 20.7 | 200.3 | 218.2 | 200.3 | NO
| NG | 108 | 76 | 76 | 9 | 20.5 | 1.86 | 50 | 68.3 | 14.6 | 66.9 | 15.9 | 199.2 | 218.9 | 199.2 | NO
7 | OK | 108 | 114 | 107 | 49 | 31.4 | 11.42 | 50 | 68.3 | 14.6 | 58.8 | 21.2 | 211.9 | 214.4 | 211.9 | YES
| NG | 57 | 61 | 65 | 12 | 138.9 | 7.9 | 50 | 68.3 | 14.6 | 62 | 20.4 | 200.2 | 218.2 | 200.2 | NO
8 | OK | 114 | 115 | 107 | 49 | 31.4 | 9.4 | 50 | 68.3 | 14.6 | 60.4 | 19.5 | 212 | 218.4 | 212 | YES
| NG | 61 | 59 | 65 | 12 | 138.9 | 6.73 | 50 | 68.3 | 14.6 | 62.9 | 17.6 | 200.4 | 218.7 | 200.4 | NO
9 | OK | 115 | 121 | 107 | 49 | 31.4 | 8.5 | 50 | 68.3 | 14.6 | 61.1 | 19.5 | 211.3 | 218.4 | 211.3 | YES
| NG | 59 | 62 | 65 | 12 | 138.9 | 3.36 | 50 | 68.3 | 14.6 | 65.5 | 17 | 200 | 218.7 | 200 | NO
| NG | 121 | 113 | 113 | 12 | 137 | 3.3 | 50 | 68.3 | 14.6 | 65.5 | 17 | 202.9 | 218.8 | 202.9 | NO
| NG | 121 | 134 | 107 | 49 | 31.4 | 4.93 | 50 | 68.3 | 14.6 | 64 | 18.3 | 209.8 | 219 | 209.8 | NO
| NG | 62 | 63 | 65 | 12 | 138.9 | 3.36 | 50 | 68.3 | 14.6 | 65.5 | 17 | 200 | 218.7 | 200 | NO
| NG | 134 | 119 | 107 | 49 | 31.4 | 3.14 | 50 | 68.3 | 14.6 | 65.5 | 16.9 | 208.8 | 219 | 208.8 | NO
| NG | 63 | 65 | 65 | 12 | 138.9 | 1.71 | 50 | 68.3 | 14.6 | 66.9 | 15.8 | 200.3 | 218.9 | 200.3 | NO
| NG | 119 | 116 | 107 | 49 | 31.4 | 1.15 | 50 | 68.3 | 14.6 | 67 | 15.4 | 203.8 | 219 | 203.8 | NO
| NG | 116 | 122 | 107 | 49 | 31.4 | 0.82 | 50 | 68.3 | 14.6 | 67.5 | 15.2 | 202.2 | 219 | 202.2 | NO
| NG | 122 | 106 | 107 | 49 | 31.4 | 0.76 | 50 | 68.3 | 14.6 | 67.6 | 15.1 | 202 | 219 | 202 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 44-000257
TR_B (available) | 66-018344
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 68.3
TR_B Baseline Loading% | 14.6
Total Scenarios Evaluated | 48
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 77
Switch Child Node | 71
Tie Node (TR_A side) | 76
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 20.5
Load Transferred (kW) | 20.03
TR_A Loading After (%) | 52.4
TR_B Loading After (%) | 29.4
Minimum Voltage (V) | 214.3