## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 29 | 27 | 28 | 13 | 46.7 | 2.23 | 50 | 68.3 | 34.8 | 66.7 | 37.5 | 199.5 | 220.8 | 199.5 | NO
| NG | 29 | 32 | 30 | 13 | 140.1 | 11.56 | 50 | 68.3 | 34.8 | 60 | 49 | 200 | 213.1 | 200 | NO
| NG | 29 | 42 | 42 | 13 | 44 | 18.85 | 50 | 68.3 | 34.8 | 54.7 | 58.8 | 200.1 | 198.6 | 198.6 | NO
| NG | 27 | 28 | 28 | 13 | 46.7 | 0.8 | 50 | 68.3 | 34.8 | 67.7 | 35.8 | 199.5 | 223.1 | 199.5 | NO
| NG | 32 | 33 | 30 | 13 | 140.1 | 0.89 | 50 | 68.3 | 34.8 | 67.6 | 35.9 | 199.5 | 223.4 | 199.5 | NO
| NG | 42 | 43 | 43 | 13 | 54.9 | 8.07 | 50 | 68.3 | 34.8 | 61.9 | 44.9 | 199.9 | 208.8 | 199.9 | NO
| NG | 42 | 127 | 127 | 13 | 45.6 | 9.33 | 50 | 68.3 | 34.8 | 61.5 | 45.2 | 199.8 | 216.4 | 199.8 | NO
| NG | 0 | 135 | 135 | 13 | 116.6 | 1.38 | 50 | 68.3 | 34.8 | 67.3 | 36.5 | 199.5 | 221.2 | 199.5 | NO
| NG | 33 | 30 | 30 | 13 | 140.1 | 0.64 | 50 | 68.3 | 34.8 | 67.8 | 35.6 | 199.5 | 224 | 199.5 | NO
| NG | 43 | 46 | 46 | 13 | 56.4 | 8.06 | 50 | 68.3 | 34.8 | 61.9 | 44.8 | 199.9 | 208.9 | 199.9 | NO
| NG | 127 | 49 | 48 | 13 | 103.2 | 9.33 | 50 | 68.3 | 34.8 | 61.5 | 45.2 | 199.8 | 216.3 | 199.8 | NO
| NG | 66 | 69 | 68 | 13 | 35.7 | 2.91 | 50 | 68.3 | 34.8 | 66.1 | 38.3 | 200.2 | 222.2 | 200.2 | NO
| NG | 135 | 31 | 31 | 13 | 121.6 | 0.85 | 50 | 68.3 | 34.8 | 67.7 | 35.8 | 199.5 | 222.4 | 199.5 | NO
| NG | 46 | 47 | 2 | 13 | 58.9 | 7.78 | 50 | 68.3 | 34.8 | 62.1 | 44.5 | 199.9 | 209.8 | 199.9 | NO
| NG | 49 | 48 | 48 | 13 | 103.2 | 1.45 | 50 | 68.3 | 34.8 | 67.2 | 35.6 | 199.6 | 222.9 | 199.6 | NO
| NG | 49 | 98 | 98 | 13 | 136.3 | 2.54 | 50 | 68.3 | 34.8 | 66.4 | 37.4 | 199.5 | 217.9 | 199.5 | NO
| NG | 69 | 68 | 68 | 13 | 35.7 | 2.14 | 50 | 68.3 | 34.8 | 66.7 | 34.8 | 200.2 | 223.9 | 200.2 | NO
| NG | 47 | 5 | 2 | 13 | 58.9 | 6.63 | 50 | 68.3 | 34.8 | 62.9 | 43.1 | 199.7 | 209.6 | 199.7 | NO
| NG | 98 | 97 | 97 | 13 | 148.3 | 2.12 | 50 | 68.3 | 34.8 | 66.7 | 37.4 | 199.5 | 218.2 | 199.5 | NO
| NG | 5 | 4 | 2 | 13 | 58.9 | 6.63 | 50 | 68.3 | 34.8 | 63.4 | 43.1 | 199.6 | 209.6 | 199.6 | NO
| NG | 97 | 102 | 102 | 13 | 149.5 | 2.12 | 50 | 68.3 | 34.8 | 66.7 | 37.4 | 199.5 | 218.2 | 199.5 | NO
| NG | 4 | 3 | 2 | 13 | 58.9 | 1.67 | 50 | 68.3 | 34.8 | 67 | 36.8 | 199.5 | 220.4 | 199.5 | NO
| NG | 4 | 105 | 105 | 13 | 94.9 | 3.08 | 50 | 68.3 | 34.8 | 65.3 | 38.5 | 199.6 | 217.8 | 199.6 | NO
| NG | 86 | 87 | 22 | 2 | 19.9 | 44.41 | 50 | 68.3 | 34.8 | 34.2 | 90 | 224.5 | 150.3 | 150.3 | NO
| NG | 105 | 44 | 44 | 13 | 100.4 | 2.72 | 50 | 68.3 | 34.8 | 66.3 | 38 | 199.6 | 218.7 | 199.6 | NO
| NG | 87 | 77 | 22 | 2 | 19.9 | 44.02 | 50 | 68.3 | 34.8 | 34.5 | 89 | 224.5 | 153 | 153 | NO
| NG | 77 | 78 | 22 | 2 | 19.9 | 23.99 | 50 | 68.3 | 34.8 | 49.8 | 58 | 204.6 | 199.1 | 199.1 | NO
1 | OK | 77 | 71 | 117 | 23 | 36.3 | 20.03 | 50 | 68.3 | 34.8 | 52.4 | 42.9 | 214.3 | 210.3 | 210.3 | YES
| NG | 78 | 92 | 22 | 2 | 19.9 | 22.97 | 50 | 68.3 | 34.8 | 50.5 | 58 | 204.6 | 199.1 | 199.1 | NO
2 | ** OPTIMAL ** | 71 | 72 | 117 | 23 | 36.3 | 18.21 | 50 | 68.3 | 34.8 | 53.7 | 41.2 | 213.4 | 214.7 | 213.4 | YES
| NG | 92 | 79 | 22 | 2 | 19.9 | 21.38 | 50 | 68.3 | 34.8 | 51.8 | 55.9 | 203.4 | 198.8 | 198.8 | NO
3 | OK | 72 | 73 | 117 | 23 | 36.3 | 17.34 | 50 | 68.3 | 34.8 | 54.4 | 40.5 | 213 | 216.4 | 213 | YES
| NG | 79 | 55 | 22 | 2 | 19.9 | 21.38 | 50 | 68.3 | 34.8 | 51.8 | 55.9 | 203.4 | 198.8 | 198.8 | NO
4 | OK | 73 | 74 | 117 | 23 | 36.3 | 16.5 | 50 | 68.3 | 34.8 | 55 | 39.9 | 212.7 | 217.8 | 212.7 | YES
| NG | 55 | 56 | 22 | 2 | 19.9 | 6.59 | 50 | 68.3 | 34.8 | 63.1 | 40.2 | 201.1 | 220.7 | 201.1 | NO
| NG | 55 | 80 | 83 | 18 | 44.3 | 5.6 | 50 | 68.3 | 34.8 | 64 | 41.3 | 200.4 | 223.6 | 200.4 | NO
5 | OK | 74 | 75 | 117 | 23 | 36.3 | 14.98 | 50 | 68.3 | 34.8 | 56.2 | 39.9 | 212.7 | 217.8 | 212.7 | YES
| NG | 56 | 54 | 22 | 2 | 19.9 | 5.01 | 50 | 68.3 | 34.8 | 64.3 | 40.2 | 201.2 | 220.7 | 201.2 | NO
| NG | 80 | 82 | 83 | 18 | 44.3 | 3.75 | 50 | 68.3 | 34.8 | 65.5 | 39.2 | 199.6 | 223.7 | 199.6 | NO
6 | OK | 75 | 108 | 117 | 23 | 36.3 | 13.28 | 50 | 68.3 | 34.8 | 57.5 | 38.7 | 212.1 | 220.3 | 212.1 | YES
| NG | 54 | 25 | 22 | 2 | 19.9 | 3.7 | 50 | 68.3 | 34.8 | 65.3 | 38.6 | 201.4 | 223 | 201.4 | NO
| NG | 82 | 81 | 83 | 18 | 44.3 | 3.75 | 50 | 68.3 | 34.8 | 65.5 | 39.2 | 199.6 | 223.7 | 199.6 | NO
7 | OK | 108 | 114 | 117 | 23 | 36.3 | 11.42 | 50 | 68.3 | 34.8 | 58.8 | 38.2 | 211.9 | 221.6 | 211.9 | YES
| NG | 25 | 24 | 22 | 2 | 19.9 | 2.91 | 50 | 68.3 | 34.8 | 65.9 | 37.7 | 201.6 | 222.8 | 201.6 | NO
| NG | 81 | 85 | 83 | 18 | 44.3 | 2.7 | 50 | 68.3 | 34.8 | 66.2 | 37.9 | 199.5 | 223.7 | 199.5 | NO
8 | OK | 114 | 115 | 117 | 23 | 36.3 | 9.4 | 50 | 68.3 | 34.8 | 60.4 | 38.2 | 212 | 221.6 | 212 | YES
| NG | 24 | 26 | 22 | 2 | 19.9 | 2.41 | 50 | 68.3 | 34.8 | 66.3 | 37.7 | 201.6 | 222.8 | 201.6 | NO
| NG | 85 | 84 | 83 | 18 | 44.3 | 1.66 | 50 | 68.3 | 34.8 | 66.4 | 36.7 | 199.5 | 223.7 | 199.5 | NO
9 | OK | 115 | 121 | 117 | 23 | 36.3 | 8.5 | 50 | 68.3 | 34.8 | 61.1 | 37.1 | 211.3 | 223.4 | 211.3 | YES
| NG | 26 | 23 | 22 | 2 | 19.9 | 1.71 | 50 | 68.3 | 34.8 | 66.3 | 36.8 | 201.6 | 223.8 | 201.6 | NO
| NG | 84 | 83 | 83 | 18 | 44.3 | 0.87 | 50 | 68.3 | 34.8 | [5 empty] | NO | TR_B sim: loading 0.9% despite baseline 34.8% (degenerate)
| NG | 121 | 113 | 117 | 23 | 36.3 | 3.3 | 50 | 68.3 | 34.8 | 65.5 | 36.7 | 202.9 | 223.5 | 202.9 | NO
| NG | 23 | 22 | 22 | 2 | 19.9 | 0.86 | 50 | 68.3 | 34.8 | 67.6 | 34.8 | 200.3 | 223.9 | 200.3 | NO
| NG | 113 | 112 | 117 | 23 | 36.3 | 3.01 | 50 | 68.3 | 34.8 | 65.7 | 36.4 | 203.1 | 223.6 | 203.1 | NO
| NG | 112 | 133 | 117 | 23 | 36.3 | 1.8 | 50 | 68.3 | 34.8 | 66.8 | 36.4 | 199.9 | 223.6 | 199.9 | NO
| NG | 133 | 110 | 117 | 23 | 36.3 | 1.58 | 50 | 68.3 | 34.8 | 66.8 | 36.4 | 199.9 | 223.6 | 199.9 | NO
| NG | 110 | 109 | 117 | 23 | 36.3 | 1.27 | 50 | 68.3 | 34.8 | 67.3 | 36.3 | 198.8 | 223.6 | 198.8 | NO
| NG | 109 | 111 | 117 | 23 | 36.3 | 1.13 | 50 | 68.3 | 34.8 | 67.3 | 36.1 | 198.8 | 223.6 | 198.8 | NO
| NG | 111 | 118 | 117 | 23 | 36.3 | 0.67 | 50 | 68.3 | 34.8 | 67.7 | 35.6 | 199.1 | 223.7 | 199.1 | NO
| NG | 118 | 117 | 117 | 23 | 36.3 | 0.57 | 50 | 68.3 | 34.8 | 67.8 | 34.8 | 199.2 | 223.9 | 199.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 44-000257
TR_B (available) | 67-004414
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 68.3
TR_B Baseline Loading% | 34.8
Total Scenarios Evaluated | 60
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 71
Switch Child Node | 72
Tie Node (TR_A side) | 117
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 36.3
Load Transferred (kW) | 18.21
TR_A Loading After (%) | 53.7
TR_B Loading After (%) | 41.2
Minimum Voltage (V) | 213.4