## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 44 | 71 | 78 | 59 | 17.2 | 16.45 | 50 | 78.9 | 49.3 | 67 | 62.8 | 218.4 | 192.6 | 192.6 | NO
| NG | 44 | 83 | 2 | 59 | 82.9 | 38.63 | 50 | 78.9 | 49.3 | 50.7 | 83.3 | 219.7 | 162.2 | 162.2 | NO
| NG | 71 | 36 | 78 | 59 | 17.2 | 16.17 | 50 | 78.9 | 49.3 | 67.2 | 62.6 | 218.4 | 192.3 | 192.3 | NO
| NG | 83 | 45 | 2 | 59 | 82.9 | 36.8 | 50 | 78.9 | 49.3 | 52 | 82.8 | 219.4 | 162 | 162 | NO
| NG | 18 | 40 | 81 | 51 | 2.9 | 41.68 | 50 | 78.9 | 49.3 | 48.4 | 83 | 220.9 | 193.5 | 193.5 | NO
1 | OK | 18 | 92 | 56 | 51 | 90.3 | 6.57 | 50 | 78.9 | 49.3 | 74.2 | 53.3 | 218.8 | 214 | 214 | YES
| NG | 36 | 35 | 78 | 59 | 17.2 | 14.18 | 50 | 78.9 | 49.3 | 68.6 | 60.7 | 218.4 | 199.7 | 199.7 | NO
2 | OK | 45 | 46 | 46 | 59 | 135.3 | 1.64 | 50 | 78.9 | 49.3 | 77.8 | 50.6 | 218.4 | 214.3 | 214.3 | YES
3 | OK | 45 | 93 | 2 | 59 | 82.9 | 3.62 | 50 | 78.9 | 49.3 | 76.3 | 52 | 218.2 | 214.8 | 214.8 | YES
| NG | 40 | 39 | 81 | 51 | 2.9 | 31.88 | 50 | 78.9 | 49.3 | 54.7 | 74.3 | 220.2 | 206.2 | 206.2 | NO
4 | OK | 40 | 86 | 91 | 51 | 88.5 | 9.8 | 50 | 78.9 | 49.3 | 71.8 | 56 | 218.3 | 214.8 | 214.8 | YES
5 | OK | 92 | 24 | 56 | 51 | 90.3 | 4.92 | 50 | 78.9 | 49.3 | 75.4 | 52 | 218.8 | 215 | 215 | YES
6 | OK | 35 | 27 | 78 | 59 | 17.2 | 11.2 | 50 | 78.9 | 49.3 | 70.8 | 57.1 | 218.4 | 212.6 | 212.6 | YES
7 | OK | 46 | 19 | 19 | 59 | 136 | 1.6 | 50 | 78.9 | 49.3 | 77.8 | 50.5 | 218.4 | 214.5 | 214.5 | YES
8 | OK | 93 | 2 | 2 | 59 | 82.9 | 1.5 | 50 | 78.9 | 49.3 | 77.8 | 50.4 | 218.2 | 215.1 | 215.1 | YES
| NG | 39 | 4 | 81 | 51 | 2.9 | 31.28 | 50 | 78.9 | 49.3 | 55.2 | 73.9 | 220.2 | 206.1 | 206.1 | NO
9 | OK | 86 | 72 | 91 | 51 | 88.5 | 8.25 | 50 | 78.9 | 49.3 | 72.9 | 54.8 | 217.7 | 214.8 | 214.8 | YES
10 | OK | 24 | 55 | 56 | 51 | 90.3 | 2.35 | 50 | 78.9 | 49.3 | 77.2 | 49.9 | 218.4 | 215 | 215 | YES
11 | OK | 27 | 28 | 78 | 59 | 17.2 | 3.77 | 50 | 78.9 | 49.3 | 76.2 | 52.1 | 218.2 | 214.7 | 214.7 | YES
12 | OK | 27 | 63 | 29 | 90 | 21.7 | 6.23 | 50 | 78.9 | 49.3 | 74.4 | 51.3 | 218.4 | 215.1 | 215.1 | YES
13 | OK | 19 | 20 | 20 | 59 | 147.8 | 1.6 | 50 | 78.9 | 49.3 | 77.8 | 50.5 | 218.4 | 214.8 | 214.8 | YES
| NG | 4 | 3 | 81 | 51 | 2.9 | 30.99 | 50 | 78.9 | 49.3 | 56.1 | 73.6 | 220.1 | 206.2 | 206.2 | NO
14 | OK | 72 | 73 | 73 | 51 | 129.2 | 1.1 | 50 | 78.9 | 49.3 | 78.1 | 49.3 | 218.1 | 215.1 | 215.1 | YES
15 | OK | 72 | 91 | 91 | 51 | 88.5 | 7.13 | 50 | 78.9 | 49.3 | 73.7 | 54.7 | 217.8 | 214.8 | 214.8 | YES
16 | OK | 55 | 60 | 59 | 51 | 96.5 | 1.84 | 50 | 78.9 | 49.3 | 77.6 | 50.6 | 218.3 | 214.9 | 214.9 | YES
17 | OK | 55 | 95 | 95 | 51 | 95.6 | 0.38 | 50 | 78.9 | 49.3 | 78.7 | 49.3 | 218.2 | 215.1 | 215.1 | YES
18 | OK | 28 | 57 | 78 | 59 | 17.2 | 3.58 | 50 | 78.9 | 49.3 | 76.3 | 52 | 218.2 | 214.7 | 214.7 | YES
19 | ** OPTIMAL ** | 63 | 1 | 29 | 90 | 21.7 | 4.31 | 50 | 78.9 | 49.3 | 75.8 | 51.3 | 218.4 | 215.1 | 215.1 | YES
| NG | 3 | 8 | 81 | 51 | 2.9 | 28.35 | 50 | 78.9 | 49.3 | 58 | 71.4 | 220.1 | 210 | 210 | NO
20 | OK | 73 | 76 | 76 | 51 | 136.7 | 1.02 | 50 | 78.9 | 49.3 | 78.2 | 49.3 | 218.1 | 215.1 | 215.1 | YES
21 | OK | 60 | 59 | 59 | 51 | 96.5 | 0.97 | 50 | 78.9 | 49.3 | 78.2 | 49.7 | 218.2 | 215 | 215 | YES
22 | OK | 57 | 58 | 78 | 59 | 17.2 | 1.27 | 50 | 78.9 | 49.3 | 78 | 50 | 218.2 | 215 | 215 | YES
23 | OK | 1 | 0 | 29 | 90 | 21.7 | 4.31 | 50 | 78.9 | 49.3 | 75.8 | 50.8 | 218.4 | 215.1 | 215.1 | YES
| NG | 8 | 7 | 81 | 51 | 2.9 | 27.77 | 50 | 78.9 | 49.3 | 58.4 | 70.9 | 220.1 | 209.7 | 209.7 | NO
24 | OK | 76 | 74 | 74 | 51 | 145 | 0.98 | 50 | 78.9 | 49.3 | 78.2 | 49.3 | 218.1 | 215.1 | 215.1 | YES
25 | OK | 58 | 98 | 78 | 59 | 17.2 | 0.47 | 50 | 78.9 | 49.3 | 78.6 | 49.6 | 218.2 | 215 | 215 | YES
26 | OK | 0 | 29 | 29 | 90 | 21.7 | 1.71 | 50 | 78.9 | 49.3 | 77.7 | 50.6 | 218.2 | 215.1 | 215.1 | YES
27 | OK | 0 | 34 | 26 | 87 | 35.7 | 1.71 | 50 | 78.9 | 49.3 | 77.7 | 50.5 | 218.3 | 215.1 | 215.1 | YES
28 | OK | 7 | 30 | 81 | 51 | 2.9 | 25.82 | 50 | 78.9 | 49.3 | 59.8 | 69.3 | 219.9 | 211.5 | 211.5 | YES
29 | OK | 7 | 82 | 13 | 51 | 131.1 | 1.95 | 50 | 78.9 | 49.3 | 77.5 | 50.7 | 217.9 | 215 | 215 | YES
30 | OK | 98 | 127 | 78 | 59 | 17.2 | 0.22 | 50 | 78.9 | 49.3 | 78.8 | 49.4 | 218.2 | 215.1 | 215.1 | YES
31 | OK | 34 | 26 | 26 | 87 | 35.7 | 0.62 | 50 | 78.9 | 49.3 | 78.5 | 49.7 | 218.2 | 215.1 | 215.1 | YES
32 | OK | 30 | 62 | 81 | 51 | 2.9 | 23.81 | 50 | 78.9 | 49.3 | 61.3 | 67.7 | 219.9 | 213 | 213 | YES
33 | OK | 82 | 12 | 13 | 51 | 131.1 | 0.36 | 50 | 78.9 | 49.3 | 77.9 | 49.5 | 218 | 215 | 215 | YES
34 | OK | 62 | 61 | 81 | 51 | 2.9 | 22.29 | 50 | 78.9 | 49.3 | 62.4 | 66.5 | 219.7 | 212.8 | 212.8 | YES
35 | OK | 12 | 13 | 13 | 51 | 131.1 | 0.05 | 50 | 78.9 | 49.3 | 78.9 | 49.3 | 218.2 | 215.1 | 215.1 | YES
36 | OK | 61 | 31 | 81 | 51 | 2.9 | 22.29 | 50 | 78.9 | 49.3 | 62.4 | 66.5 | 219.7 | 212.8 | 212.8 | YES
37 | OK | 31 | 11 | 81 | 51 | 2.9 | 11.63 | 50 | 78.9 | 49.3 | 70.2 | 58.1 | 219.2 | 213.5 | 213.5 | YES
38 | OK | 31 | 48 | 84 | 6 | 41.3 | 10.66 | 50 | 78.9 | 49.3 | 71 | 53.2 | 218.4 | 214.3 | 214.3 | YES
39 | OK | 11 | 10 | 10 | 51 | 35.4 | 2.26 | 50 | 78.9 | 49.3 | 74.9 | 50.9 | 218.4 | 215 | 215 | YES
40 | OK | 11 | 9 | 81 | 51 | 2.9 | 7.53 | 50 | 78.9 | 49.3 | 73.3 | 54 | 219.2 | 214.8 | 214.8 | YES
41 | OK | 48 | 49 | 84 | 6 | 41.3 | 9.44 | 50 | 78.9 | 49.3 | 71.9 | 52.3 | 218.5 | 214.5 | 214.5 | YES
42 | OK | 9 | 33 | 33 | 51 | 44.1 | 3.38 | 50 | 78.9 | 49.3 | 76.4 | 51.8 | 218.6 | 214.8 | 214.8 | YES
43 | OK | 49 | 64 | 84 | 6 | 41.3 | 8.05 | 50 | 78.9 | 49.3 | 72.9 | 52.1 | 218.3 | 214.5 | 214.5 | YES
44 | OK | 33 | 6 | 32 | 124 | 59.1 | 2.41 | 50 | 78.9 | 49.3 | 77.1 | 50.6 | 218.4 | 214.8 | 214.8 | YES
| NG | 64 | 66 | 70 | 6 | 55.3 | 2.64 | 50 | 78.9 | 49.3 | 0 | 50 | 5.4 | 214.9 | 5.4 | NO
45 | OK | 64 | 85 | 85 | 121 | 113.3 | 2.81 | 50 | 78.9 | 49.3 | 76.8 | 51.4 | 218 | 214.7 | 214.7 | YES
| NG | 64 | 90 | 84 | 6 | 41.3 | 2.6 | 50 | 78.9 | 49.3 | 77 | 1132.2 | 218.6 | 9.2 | 9.2 | NO
46 | OK | 6 | 5 | 32 | 124 | 59.1 | 1.76 | 50 | 78.9 | 49.3 | 77.6 | 50.6 | 218.1 | 214.8 | 214.8 | YES
| NG | 66 | 67 | 70 | 6 | 55.3 | 1.59 | 50 | 78.9 | 49.3 | [5 empty] | NO | TR_A sim: loading 3089% (degenerate)
47 | OK | 85 | 94 | 94 | 121 | 122.7 | 1.42 | 50 | 78.9 | 49.3 | 77.9 | 50.3 | 218.1 | 214.9 | 214.9 | YES
48 | OK | 90 | 84 | 84 | 6 | 41.3 | 0.53 | 50 | 78.9 | 49.3 | 78.5 | 49.3 | 218.8 | 215.1 | 215.1 | YES
49 | OK | 5 | 25 | 32 | 124 | 59.1 | 1.76 | 50 | 78.9 | 49.3 | 77.6 | 50.6 | 218.1 | 214.8 | 214.8 | YES
50 | OK | 67 | 68 | 70 | 6 | 55.3 | 0.45 | 50 | 78.9 | 49.3 | 77.6 | 49.3 | 218.1 | 215.1 | 215.1 | YES
51 | OK | 25 | 32 | 32 | 124 | 59.1 | 0.21 | 50 | 78.9 | 49.3 | 78.8 | 49.4 | 218.1 | 215.1 | 215.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 44-000345
TR_B (available) | 59-003314
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 49.3
Total Scenarios Evaluated | 65
Feasible Scenarios | 51
--- Optimal Solution ---
Switch Parent Node | 63
Switch Child Node | 1
Tie Node (TR_A side) | 29
Tie Node (TR_B side) | 90
Tie Line Distance (m) | 21.7
Load Transferred (kW) | 4.31
TR_A Loading After (%) | 75.8
TR_B Loading After (%) | 51.3
Minimum Voltage (V) | 215.1