## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 44 | 71 | 78 | 38 | 3.2 | 16.45 | 50 | 78.9 | 60.1 | 67 | 81.1 | 218.4 | 198.5 | 198.5 | NO
| NG | 71 | 36 | 78 | 38 | 3.2 | 16.17 | 50 | 78.9 | 60.1 | 67.2 | 80.8 | 218.4 | 198.4 | 198.4 | NO
| NG | 36 | 35 | 78 | 38 | 3.2 | 14.18 | 50 | 78.9 | 60.1 | 68.6 | 78 | 218.4 | 203.7 | 203.7 | NO
1 | OK | 45 | 46 | 21 | 86 | 2.8 | 1.64 | 95 | 78.9 | 60.1 | 77.8 | 62 | 218.4 | 218.7 | 218.4 | YES
2 | OK | 45 | 93 | 2 | 39 | 70.9 | 3.62 | 50 | 78.9 | 60.1 | 76.3 | 62.6 | 218.2 | 217 | 217 | YES
3 | OK | 35 | 27 | 78 | 38 | 3.2 | 11.2 | 50 | 78.9 | 60.1 | 70.8 | 72.4 | 218.4 | 213.9 | 213.9 | YES
4 | OK | 46 | 19 | 21 | 86 | 2.8 | 1.6 | 95 | 78.9 | 60.1 | 77.8 | 62 | 218.4 | 218.7 | 218.4 | YES
5 | OK | 93 | 2 | 2 | 39 | 70.9 | 1.5 | 50 | 78.9 | 60.1 | 77.8 | 60.1 | 218.2 | 219.1 | 218.2 | YES
6 | OK | 79 | 47 | 47 | 86 | 88.9 | 4.63 | 50 | 78.9 | 60.1 | 75.5 | 65.5 | 218.1 | 219.2 | 218.1 | YES
7 | OK | 27 | 28 | 78 | 38 | 3.2 | 3.77 | 50 | 78.9 | 60.1 | 76.2 | 64.7 | 218.2 | 217.4 | 217.4 | YES
8 | OK | 27 | 63 | 29 | 38 | 95.5 | 6.23 | 50 | 78.9 | 60.1 | 74.4 | 63.3 | 218.4 | 217.7 | 217.7 | YES
9 | OK | 19 | 20 | 20 | 86 | 26.4 | 1.6 | 50 | 78.9 | 60.1 | 77.8 | 62 | 218.4 | 218.7 | 218.4 | YES
10 | OK | 47 | 14 | 17 | 86 | 115.2 | 2.97 | 50 | 78.9 | 60.1 | 76.8 | 63.6 | 218.2 | 219.2 | 218.2 | YES
11 | OK | 28 | 57 | 78 | 38 | 3.2 | 3.58 | 50 | 78.9 | 60.1 | 76.3 | 64.5 | 218.2 | 217.4 | 217.4 | YES
12 | OK | 63 | 1 | 29 | 38 | 95.5 | 4.31 | 50 | 78.9 | 60.1 | 75.8 | 63.3 | 218.4 | 217.7 | 217.7 | YES
13 | OK | 20 | 37 | 50 | 86 | 41.1 | 1.51 | 50 | 78.9 | 60.1 | 77.9 | 61.9 | 218.4 | 218.7 | 218.4 | YES
14 | OK | 14 | 15 | 17 | 86 | 115.2 | 2.27 | 50 | 78.9 | 60.1 | 77.3 | 62.7 | 218.2 | 219.1 | 218.2 | YES
15 | OK | 57 | 58 | 78 | 38 | 3.2 | 1.27 | 50 | 78.9 | 60.1 | 78 | 61.3 | 218.2 | 219.1 | 218.2 | YES
16 | OK | 1 | 0 | 29 | 38 | 95.5 | 4.31 | 50 | 78.9 | 60.1 | 75.8 | 62.5 | 218.4 | 218.7 | 218.4 | YES
17 | OK | 37 | 38 | 38 | 86 | 57.3 | 0.98 | 50 | 78.9 | 60.1 | 78.2 | 61.2 | 218.3 | 218.9 | 218.3 | YES
18 | OK | 37 | 50 | 50 | 86 | 41.1 | 0.43 | 50 | 78.9 | 60.1 | 78.6 | 60.6 | 218.2 | 219 | 218.2 | YES
19 | OK | 15 | 16 | 17 | 86 | 115.2 | 1.57 | 50 | 78.9 | 60.1 | 77.8 | 61.9 | 218.2 | 219.1 | 218.2 | YES
20 | OK | 58 | 98 | 78 | 38 | 3.2 | 0.47 | 50 | 78.9 | 60.1 | 78.6 | 60.7 | 218.2 | 219.1 | 218.2 | YES
21 | OK | 0 | 29 | 29 | 38 | 95.5 | 1.71 | 50 | 78.9 | 60.1 | 77.7 | 62.2 | 218.2 | 219 | 218.2 | YES
22 | OK | 0 | 34 | 34 | 38 | 148.5 | 1.71 | 50 | 78.9 | 60.1 | 77.7 | 62.2 | 218.3 | 217.8 | 217.8 | YES
23 | OK | 50 | 51 | 51 | 23 | 43 | 0.3 | 50 | 78.9 | 60.1 | 78.7 | 60.5 | 218.2 | 219 | 218.2 | YES
24 | OK | 16 | 17 | 17 | 86 | 115.2 | 0.46 | 50 | 78.9 | 60.1 | 78.6 | 60.6 | 218.2 | 219.1 | 218.2 | YES
25 | OK | 120 | 103 | 122 | 10 | 32.6 | 9.48 | 50 | 78.9 | 60.1 | 71.9 | 64.3 | 218.6 | 216.6 | 216.6 | YES
26 | OK | 98 | 127 | 78 | 38 | 3.2 | 0.22 | 50 | 78.9 | 60.1 | 78.8 | 60.4 | 218.2 | 219 | 218.2 | YES
27 | OK | 103 | 104 | 122 | 10 | 32.6 | 9.23 | 50 | 78.9 | 60.1 | 72.1 | 64.2 | 218.6 | 216.7 | 216.7 | YES
28 | OK | 104 | 109 | 122 | 10 | 32.6 | 9.23 | 50 | 78.9 | 60.1 | 72.1 | 64.2 | 218.6 | 216.7 | 216.7 | YES
29 | OK | 109 | 108 | 108 | 100 | 58.1 | 0.29 | 50 | 78.9 | 60.1 | 78.7 | 60.2 | 218.2 | 219.1 | 218.2 | YES
30 | OK | 109 | 112 | 122 | 10 | 32.6 | 8.1 | 50 | 78.9 | 60.1 | 72.9 | 64.2 | 218.6 | 216.7 | 216.7 | YES
31 | OK | 112 | 113 | 121 | 100 | 38 | 1.81 | 50 | 78.9 | 60.1 | 77.6 | 60.7 | 218.2 | 219 | 218.2 | YES
32 | OK | 112 | 114 | 122 | 10 | 32.6 | 6.29 | 50 | 78.9 | 60.1 | 74.3 | 63.1 | 218.5 | 217.8 | 217.8 | YES
33 | OK | 113 | 121 | 121 | 100 | 38 | 1.42 | 50 | 78.9 | 60.1 | 77.9 | 60.6 | 218.2 | 219 | 218.2 | YES
34 | OK | 114 | 110 | 122 | 10 | 32.6 | 5.72 | 50 | 78.9 | 60.1 | 74.7 | 63.1 | 218.5 | 217.8 | 217.8 | YES
35 | ** OPTIMAL ** | 110 | 111 | 111 | 100 | 101.8 | 4.07 | 50 | 78.9 | 60.1 | 75.9 | 63.2 | 218.5 | 218.4 | 218.4 | YES
36 | OK | 110 | 115 | 122 | 10 | 32.6 | 1.65 | 50 | 78.9 | 60.1 | 77.7 | 62.1 | 218.1 | 218.7 | 218.1 | YES
37 | OK | 115 | 122 | 122 | 10 | 32.6 | 0.39 | 50 | 78.9 | 60.1 | 78.7 | 60.6 | 218.2 | 219.1 | 218.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 44-000345
TR_B (available) | 62-001072
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 60.1
Total Scenarios Evaluated | 40
Feasible Scenarios | 37
--- Optimal Solution ---
Switch Parent Node | 110
Switch Child Node | 111
Tie Node (TR_A side) | 111
Tie Node (TR_B side) | 100
Tie Line Distance (m) | 101.8
Load Transferred (kW) | 4.07
TR_A Loading After (%) | 75.9
TR_B Loading After (%) | 63.2
Minimum Voltage (V) | 218.4