## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 42 | 41 | 96 | 52 | 36.3 | 50.52 | 50 | 78.9 | 27.6 | 42 | 95.5 | 221 | 166 | 166 | NO
| NG | 44 | 83 | 125 | 52 | 137.5 | 38.63 | 95 | 78.9 | 27.6 | 50.7 | 76.6 | 219.7 | 181.8 | 181.8 | NO
| NG | 41 | 18 | 96 | 52 | 36.3 | 49.71 | 50 | 78.9 | 27.6 | 42.5 | 94.2 | 220.9 | 166.1 | 166.1 | NO
| NG | 83 | 45 | 125 | 52 | 137.5 | 36.8 | 95 | 78.9 | 27.6 | 52 | 75.9 | 219.4 | 181.7 | 181.7 | NO
| NG | 18 | 40 | 96 | 52 | 36.3 | 41.68 | 50 | 78.9 | 27.6 | 48.4 | 82 | 220.9 | 187 | 187 | NO
1 | OK | 18 | 92 | 56 | 52 | 149.3 | 6.57 | 50 | 78.9 | 27.6 | 74.2 | 34 | 218.8 | 216.2 | 216.2 | YES
| NG | 45 | 79 | 125 | 52 | 137.5 | 29.58 | 95 | 78.9 | 27.6 | 57.2 | 65.1 | 219.2 | 195.6 | 195.6 | NO
| NG | 40 | 39 | 96 | 52 | 36.3 | 31.88 | 50 | 78.9 | 27.6 | 54.7 | 67.7 | 220.2 | 201 | 201 | NO
2 | OK | 40 | 86 | 73 | 52 | 111.2 | 9.8 | 50 | 78.9 | 27.6 | 71.8 | 30.5 | 218.3 | 214.7 | 214.7 | YES
3 | OK | 92 | 24 | 56 | 52 | 149.3 | 4.92 | 50 | 78.9 | 27.6 | 75.4 | 31.9 | 218.8 | 216.3 | 216.3 | YES
| NG | 79 | 87 | 125 | 52 | 137.5 | 24.71 | 95 | 78.9 | 27.6 | 60.8 | 58.2 | 219.2 | 206.1 | 206.1 | NO
| NG | 39 | 4 | 96 | 52 | 36.3 | 31.28 | 50 | 78.9 | 27.6 | 55.2 | 66.9 | 220.2 | 200.9 | 200.9 | NO
4 | OK | 86 | 72 | 73 | 52 | 111.2 | 8.25 | 50 | 78.9 | 27.6 | 72.9 | 30.5 | 217.7 | 214.7 | 214.7 | YES
5 | OK | 24 | 55 | 56 | 52 | 149.3 | 2.35 | 50 | 78.9 | 27.6 | 77.2 | 28.7 | 218.4 | 216 | 216 | YES
6 | OK | 87 | 88 | 125 | 52 | 137.5 | 23.45 | 95 | 78.9 | 27.6 | 61.7 | 56.5 | 219.2 | 210.1 | 210.1 | YES
| NG | 4 | 3 | 96 | 52 | 36.3 | 30.99 | 50 | 78.9 | 27.6 | 56.1 | 66.5 | 220.1 | 201 | 201 | NO
7 | OK | 72 | 73 | 73 | 52 | 111.2 | 1.1 | 50 | 78.9 | 27.6 | 78.1 | 27.8 | 218.1 | 216.1 | 216.1 | YES
8 | OK | 72 | 91 | 91 | 52 | 133.9 | 7.13 | 50 | 78.9 | 27.6 | 73.7 | 36.2 | 217.8 | 214.9 | 214.9 | YES
9 | OK | 88 | 89 | 125 | 52 | 137.5 | 23.26 | 95 | 78.9 | 27.6 | 61.8 | 56.2 | 219.2 | 210.1 | 210.1 | YES
| NG | 3 | 8 | 96 | 52 | 36.3 | 28.35 | 50 | 78.9 | 27.6 | 58 | 62.8 | 220.1 | 209.8 | 209.8 | NO
10 | ** OPTIMAL ** | 3 | 23 | 22 | 52 | 79.5 | 2.64 | 95 | 78.9 | 27.6 | 77 | 30.8 | 218.7 | 216.5 | 216.5 | YES
11 | OK | 73 | 76 | 76 | 52 | 112.9 | 1.02 | 50 | 78.9 | 27.6 | 78.2 | 27.7 | 218.1 | 216.2 | 216.2 | YES
| NG | 89 | 120 | 125 | 52 | 137.5 | 22.97 | 95 | 78.9 | 27.6 | 62 | 55.9 | 219.2 | 209.9 | 209.9 | NO
| NG | 8 | 7 | 96 | 52 | 36.3 | 27.77 | 50 | 78.9 | 27.6 | 58.4 | 62 | 220.1 | 209.9 | 209.9 | NO
12 | OK | 23 | 22 | 22 | 52 | 79.5 | 1.05 | 95 | 78.9 | 27.6 | 78.2 | 28.9 | 218.7 | 216.3 | 216.3 | YES
13 | OK | 76 | 74 | 74 | 52 | 115.3 | 0.98 | 50 | 78.9 | 27.6 | 78.2 | 27.6 | 218.1 | 216.2 | 216.2 | YES
14 | OK | 120 | 100 | 125 | 52 | 137.5 | 13.49 | 95 | 78.9 | 27.6 | 68.9 | 43.8 | 218.7 | 214 | 214 | YES
| NG | 7 | 30 | 96 | 52 | 36.3 | 25.82 | 50 | 78.9 | 27.6 | 59.8 | 59.5 | 219.9 | 209 | 209 | NO
15 | OK | 7 | 82 | 13 | 52 | 67.7 | 1.95 | 50 | 78.9 | 27.6 | 77.5 | 29.9 | 217.9 | 216 | 216 | YES
16 | OK | 74 | 75 | 75 | 52 | 118.7 | 0.98 | 50 | 78.9 | 27.6 | 78.2 | 27.6 | 218.1 | 216.2 | 216.2 | YES
17 | OK | 100 | 99 | 125 | 52 | 137.5 | 12.17 | 95 | 78.9 | 27.6 | 69.9 | 42.1 | 218.7 | 214.3 | 214.3 | YES
18 | OK | 30 | 62 | 96 | 52 | 36.3 | 23.81 | 50 | 78.9 | 27.6 | 61.3 | 56.8 | 219.9 | 210.9 | 210.9 | YES
19 | OK | 82 | 12 | 13 | 52 | 67.7 | 0.36 | 50 | 78.9 | 27.6 | 77.9 | 28.1 | 218 | 216 | 216 | YES
| NG | 99 | 119 | 125 | 52 | 137.5 | 6.86 | 95 | 78.9 | 27.6 | [5 empty] | NO | TR_A sim: loading 7714% (degenerate)
20 | OK | 62 | 61 | 96 | 52 | 36.3 | 22.29 | 50 | 78.9 | 27.6 | 62.4 | 54.9 | 219.7 | 210.5 | 210.5 | YES
21 | OK | 12 | 13 | 13 | 52 | 67.7 | 0.05 | 50 | 78.9 | 27.6 | 78.9 | 27.6 | 218.2 | 216.2 | 216.2 | YES
22 | OK | 119 | 118 | 125 | 52 | 137.5 | 6.2 | 95 | 78.9 | 27.6 | 74.3 | 35 | 218.4 | 214.5 | 214.5 | YES
23 | OK | 61 | 31 | 96 | 52 | 36.3 | 22.29 | 50 | 78.9 | 27.6 | 62.4 | 54.9 | 219.7 | 210.5 | 210.5 | YES
24 | OK | 118 | 117 | 125 | 52 | 137.5 | 4.57 | 95 | 78.9 | 27.6 | 75.5 | 33.1 | 218.1 | 214.4 | 214.4 | YES
25 | OK | 31 | 11 | 11 | 54 | 93.6 | 11.63 | 50 | 78.9 | 27.6 | 70.2 | 41.5 | 219.2 | 215.1 | 215.1 | YES
26 | OK | 31 | 48 | 96 | 52 | 36.3 | 10.66 | 50 | 78.9 | 27.6 | 71 | 40.4 | 218.4 | 212.8 | 212.8 | YES
27 | OK | 117 | 116 | 125 | 52 | 137.5 | 3.43 | 95 | 78.9 | 27.6 | 76.4 | 31.7 | 218.1 | 215.1 | 215.1 | YES
28 | OK | 11 | 10 | 10 | 54 | 113.1 | 2.26 | 50 | 78.9 | 27.6 | 74.9 | 30.3 | 218.4 | 216.1 | 216.1 | YES
29 | OK | 11 | 9 | 52 | 54 | 131.7 | 7.53 | 50 | 78.9 | 27.6 | 73.3 | 35 | 219.2 | 214.9 | 214.9 | YES
30 | OK | 48 | 49 | 96 | 52 | 36.3 | 9.44 | 50 | 78.9 | 27.6 | 71.9 | 38.9 | 218.5 | 213.7 | 213.7 | YES
31 | OK | 116 | 125 | 125 | 52 | 137.5 | 2.67 | 95 | 78.9 | 27.6 | 76.9 | 30.8 | 218.1 | 215.6 | 215.6 | YES
32 | OK | 49 | 64 | 96 | 52 | 36.3 | 8.05 | 50 | 78.9 | 27.6 | 72.9 | 37.2 | 218.3 | 213.8 | 213.8 | YES
| NG | 64 | 66 | 66 | 54 | 42.6 | 2.64 | 50 | 78.9 | 27.6 | [5 empty] | NO | TR_A sim: loading 2620% (degenerate)
33 | OK | 64 | 85 | 96 | 52 | 36.3 | 2.81 | 50 | 78.9 | 27.6 | 76.8 | 31 | 218 | 214.3 | 214.3 | YES
| NG | 64 | 90 | 90 | 54 | 41.3 | 2.6 | 50 | 78.9 | 27.6 | [5 empty] | NO | TR_B sim: loading 0.1% despite baseline 27.6% (degenerate)
| NG | 66 | 67 | 67 | 54 | 43.8 | 1.59 | 50 | 78.9 | 27.6 | [5 empty] | NO | TR_A sim: loading 3089% (degenerate)
34 | OK | 85 | 94 | 96 | 52 | 36.3 | 1.42 | 50 | 78.9 | 27.6 | 77.9 | 29.3 | 218.1 | 215.3 | 215.3 | YES
35 | OK | 90 | 84 | 84 | 54 | 55.4 | 0.53 | 50 | 78.9 | 27.6 | 78.5 | 28.3 | 218.8 | 216.3 | 216.3 | YES
| NG | 67 | 68 | 68 | 54 | 45.2 | 0.45 | 50 | 78.9 | 27.6 | 0 | 28.2 | 5.1 | 216.2 | 5.1 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 44-000345
TR_B (available) | 64-021430
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 27.6
Total Scenarios Evaluated | 54
Feasible Scenarios | 35
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 23
Tie Node (TR_A side) | 22
Tie Node (TR_B side) | 52
Tie Line Distance (m) | 79.5
Load Transferred (kW) | 2.64
TR_A Loading After (%) | 77
TR_B Loading After (%) | 30.8
Minimum Voltage (V) | 216.5