## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 43 | 42 | 22 | 66 | 14.3 | 53.19 | 95 | 78.9 | 43.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 43 | 44 | 102 | 13 | 1.2 | 55.08 | 50 | 78.9 | 43.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 42 | 41 | 22 | 66 | 14.3 | 50.52 | 95 | 78.9 | 43.2 | 42 | 80.4 | 221 | 209.5 | 209.5 | NO
| NG | 44 | 83 | 102 | 13 | 1.2 | 38.63 | 50 | 78.9 | 43.2 | 50.7 | 71.9 | 219.7 | 205.8 | 205.8 | NO
| NG | 41 | 18 | 22 | 66 | 14.3 | 49.71 | 95 | 78.9 | 43.2 | 42.5 | 79.8 | 220.9 | 209.5 | 209.5 | NO
| NG | 83 | 45 | 102 | 13 | 1.2 | 36.8 | 50 | 78.9 | 43.2 | 52 | 71.5 | 219.4 | 205.7 | 205.7 | NO
1 | OK | 18 | 40 | 22 | 66 | 14.3 | 41.68 | 95 | 78.9 | 43.2 | 48.4 | 74.5 | 220.9 | 212.9 | 212.9 | YES
2 | OK | 18 | 92 | 56 | 65 | 111.8 | 6.57 | 50 | 78.9 | 43.2 | 74.2 | 47.1 | 218.8 | 219.2 | 218.8 | YES
3 | OK | 45 | 46 | 38 | 53 | 85.1 | 1.64 | 50 | 78.9 | 43.2 | 77.8 | 44.4 | 218.4 | 219 | 218.4 | YES
4 | OK | 45 | 93 | 93 | 53 | 145.5 | 3.62 | 50 | 78.9 | 43.2 | 76.3 | 45.9 | 218.2 | 219.9 | 218.2 | YES
5 | OK | 45 | 79 | 102 | 13 | 1.2 | 29.58 | 50 | 78.9 | 43.2 | 57.2 | 65.7 | 219.2 | 210.9 | 210.9 | YES
6 | OK | 40 | 39 | 22 | 66 | 14.3 | 31.88 | 95 | 78.9 | 43.2 | 54.7 | 67 | 220.2 | 215.4 | 215.4 | YES
7 | OK | 40 | 86 | 75 | 66 | 59.4 | 9.8 | 50 | 78.9 | 43.2 | 71.8 | 44.9 | 218.3 | 219.8 | 218.3 | YES
8 | OK | 92 | 24 | 56 | 65 | 111.8 | 4.92 | 50 | 78.9 | 43.2 | 75.4 | 45.8 | 218.8 | 219.4 | 218.8 | YES
9 | OK | 46 | 19 | 38 | 53 | 85.1 | 1.6 | 50 | 78.9 | 43.2 | 77.8 | 44.4 | 218.4 | 219.1 | 218.4 | YES
10 | OK | 79 | 47 | 17 | 53 | 57.9 | 4.63 | 50 | 78.9 | 43.2 | 75.5 | 46.7 | 218.1 | 217.7 | 217.7 | YES
11 | OK | 79 | 87 | 102 | 13 | 1.2 | 24.71 | 50 | 78.9 | 43.2 | 60.8 | 61.8 | 219.2 | 216.9 | 216.9 | YES
12 | OK | 39 | 4 | 22 | 66 | 14.3 | 31.28 | 95 | 78.9 | 43.2 | 55.2 | 66.6 | 220.2 | 215.4 | 215.4 | YES
13 | OK | 86 | 72 | 75 | 66 | 59.4 | 8.25 | 50 | 78.9 | 43.2 | 72.9 | 44.9 | 217.7 | 219.8 | 217.7 | YES
14 | OK | 24 | 55 | 56 | 65 | 111.8 | 2.35 | 50 | 78.9 | 43.2 | 77.2 | 43.9 | 218.4 | 219.8 | 218.4 | YES
15 | OK | 19 | 20 | 38 | 53 | 85.1 | 1.6 | 50 | 78.9 | 43.2 | 77.8 | 44.4 | 218.4 | 219.1 | 218.4 | YES
16 | OK | 47 | 14 | 17 | 53 | 57.9 | 2.97 | 50 | 78.9 | 43.2 | 76.8 | 45.4 | 218.2 | 220.1 | 218.2 | YES
17 | OK | 87 | 88 | 102 | 13 | 1.2 | 23.45 | 50 | 78.9 | 43.2 | 61.7 | 60.8 | 219.2 | 216.9 | 216.9 | YES
18 | OK | 4 | 3 | 22 | 66 | 14.3 | 30.99 | 95 | 78.9 | 43.2 | 56.1 | 66.3 | 220.1 | 215.4 | 215.4 | YES
19 | OK | 72 | 73 | 75 | 66 | 59.4 | 1.1 | 50 | 78.9 | 43.2 | 78.1 | 43.3 | 218.1 | 219.8 | 218.1 | YES
20 | OK | 72 | 91 | 91 | 65 | 96.8 | 7.13 | 50 | 78.9 | 43.2 | 73.7 | 48.4 | 217.8 | 219.8 | 217.8 | YES
21 | OK | 55 | 60 | 59 | 65 | 121.7 | 1.84 | 50 | 78.9 | 43.2 | 77.6 | 44.5 | 218.3 | 219.7 | 218.3 | YES
22 | OK | 55 | 95 | 95 | 65 | 132.1 | 0.38 | 50 | 78.9 | 43.2 | 78.7 | 43.2 | 218.2 | 219.8 | 218.2 | YES
23 | OK | 20 | 37 | 38 | 53 | 85.1 | 1.51 | 50 | 78.9 | 43.2 | 77.9 | 44.4 | 218.4 | 219.1 | 218.4 | YES
24 | OK | 14 | 15 | 17 | 53 | 57.9 | 2.27 | 50 | 78.9 | 43.2 | 77.3 | 44.9 | 218.2 | 220.1 | 218.2 | YES
25 | OK | 88 | 89 | 102 | 13 | 1.2 | 23.26 | 50 | 78.9 | 43.2 | 61.8 | 60.7 | 219.2 | 216.9 | 216.9 | YES
26 | OK | 3 | 8 | 96 | 65 | 20.1 | 28.35 | 50 | 78.9 | 43.2 | 58 | 64.3 | 220.1 | 216.9 | 216.9 | YES
27 | OK | 3 | 23 | 22 | 66 | 14.3 | 2.64 | 95 | 78.9 | 43.2 | 77 | 45.1 | 218.7 | 219.5 | 218.7 | YES
28 | OK | 73 | 76 | 75 | 66 | 59.4 | 1.02 | 50 | 78.9 | 43.2 | 78.2 | 43.2 | 218.1 | 219.8 | 218.1 | YES
29 | OK | 60 | 59 | 59 | 65 | 121.7 | 0.97 | 50 | 78.9 | 43.2 | 78.2 | 43.7 | 218.2 | 219.8 | 218.2 | YES
30 | OK | 37 | 38 | 38 | 53 | 85.1 | 0.98 | 50 | 78.9 | 43.2 | 78.2 | 44 | 218.3 | 219.4 | 218.3 | YES
31 | OK | 37 | 50 | 50 | 53 | 109.1 | 0.43 | 50 | 78.9 | 43.2 | 78.6 | 43.5 | 218.2 | 219.6 | 218.2 | YES
32 | OK | 15 | 16 | 17 | 53 | 57.9 | 1.57 | 50 | 78.9 | 43.2 | 77.8 | 44.4 | 218.2 | 220 | 218.2 | YES
33 | OK | 89 | 120 | 102 | 13 | 1.2 | 22.97 | 50 | 78.9 | 43.2 | 62 | 60.4 | 219.2 | 217 | 217 | YES
34 | OK | 8 | 7 | 96 | 65 | 20.1 | 27.77 | 50 | 78.9 | 43.2 | 58.4 | 63.9 | 220.1 | 216.6 | 216.6 | YES
35 | OK | 23 | 22 | 22 | 66 | 14.3 | 1.05 | 95 | 78.9 | 43.2 | 78.2 | 44 | 218.7 | 219.7 | 218.7 | YES
36 | OK | 76 | 74 | 75 | 66 | 59.4 | 0.98 | 50 | 78.9 | 43.2 | 78.2 | 43.2 | 218.1 | 219.8 | 218.1 | YES
37 | OK | 50 | 51 | 51 | 53 | 132.2 | 0.3 | 50 | 78.9 | 43.2 | 78.7 | 43.4 | 218.2 | 219.7 | 218.2 | YES
38 | OK | 16 | 17 | 17 | 53 | 57.9 | 0.46 | 50 | 78.9 | 43.2 | 78.6 | 43.6 | 218.2 | 219.9 | 218.2 | YES
39 | OK | 120 | 100 | 102 | 13 | 1.2 | 13.49 | 50 | 78.9 | 43.2 | 68.9 | 53.2 | 218.7 | 218.4 | 218.4 | YES
40 | OK | 120 | 103 | 103 | 53 | 6 | 9.48 | 50 | 78.9 | 43.2 | 71.9 | 50.3 | 218.6 | 218.4 | 218.4 | YES
41 | OK | 7 | 30 | 96 | 65 | 20.1 | 25.82 | 50 | 78.9 | 43.2 | 59.8 | 62.4 | 219.9 | 216.8 | 216.8 | YES
42 | OK | 7 | 82 | 82 | 66 | 21.3 | 1.95 | 50 | 78.9 | 43.2 | 77.5 | 44.6 | 217.9 | 219.8 | 217.9 | YES
43 | OK | 74 | 75 | 75 | 66 | 59.4 | 0.98 | 50 | 78.9 | 43.2 | 78.2 | 43.2 | 218.1 | 219.8 | 218.1 | YES
44 | OK | 100 | 99 | 102 | 13 | 1.2 | 12.17 | 50 | 78.9 | 43.2 | 69.9 | 52.3 | 218.7 | 218.6 | 218.6 | YES
45 | OK | 103 | 104 | 104 | 53 | 16.1 | 9.23 | 50 | 78.9 | 43.2 | 72.1 | 50.1 | 218.6 | 218.5 | 218.5 | YES
46 | OK | 30 | 62 | 96 | 65 | 20.1 | 23.81 | 50 | 78.9 | 43.2 | 61.3 | 60.8 | 219.9 | 218.8 | 218.8 | YES
47 | OK | 82 | 12 | 13 | 65 | 25.8 | 0.36 | 50 | 78.9 | 43.2 | 77.9 | 43.5 | 218 | 219.8 | 218 | YES
48 | OK | 99 | 107 | 106 | 82 | 75.7 | 3.25 | 50 | 78.9 | 43.2 | 76.5 | 44.9 | 218.3 | 219.8 | 218.3 | YES
| NG | 99 | 119 | 125 | 82 | 4.5 | 6.86 | 95 | 78.9 | 43.2 | 0 | 48.2 | 16.6 | 219.6 | 16.6 | NO
49 | OK | 99 | 101 | 102 | 13 | 1.2 | 1.82 | 50 | 78.9 | 43.2 | 77.6 | 44.6 | 218.3 | 219.5 | 218.3 | YES
50 | OK | 104 | 109 | 111 | 5 | 30.8 | 9.23 | 50 | 78.9 | 43.2 | 72.1 | 50.1 | 218.6 | 218.5 | 218.5 | YES
51 | OK | 62 | 61 | 96 | 65 | 20.1 | 22.29 | 50 | 78.9 | 43.2 | 62.4 | 59.7 | 219.7 | 218.8 | 218.8 | YES
52 | OK | 12 | 13 | 13 | 65 | 25.8 | 0.05 | 50 | 78.9 | 43.2 | 78.9 | 43.2 | 218.2 | 219.8 | 218.2 | YES
53 | OK | 107 | 105 | 106 | 82 | 75.7 | 2.31 | 50 | 78.9 | 43.2 | 77.2 | 44.9 | 218.2 | 219.8 | 218.2 | YES
54 | OK | 119 | 118 | 125 | 82 | 4.5 | 6.2 | 95 | 78.9 | 43.2 | 74.3 | 47.7 | 218.4 | 219.6 | 218.4 | YES
55 | OK | 109 | 108 | 108 | 53 | 67.2 | 0.29 | 50 | 78.9 | 43.2 | 78.7 | 43.4 | 218.2 | 219.8 | 218.2 | YES
56 | OK | 109 | 112 | 111 | 5 | 30.8 | 8.1 | 50 | 78.9 | 43.2 | 72.9 | 49.3 | 218.6 | 218.5 | 218.5 | YES
57 | OK | 61 | 31 | 96 | 65 | 20.1 | 22.29 | 50 | 78.9 | 43.2 | 62.4 | 59.7 | 219.7 | 218.8 | 218.8 | YES
58 | OK | 105 | 106 | 106 | 82 | 75.7 | 1.2 | 50 | 78.9 | 43.2 | 78 | 44.1 | 218.2 | 219.8 | 218.2 | YES
59 | OK | 118 | 117 | 125 | 82 | 4.5 | 4.57 | 95 | 78.9 | 43.2 | 75.5 | 46.5 | 218.1 | 219.8 | 218.1 | YES
60 | OK | 118 | 126 | 124 | 9 | 29.8 | 1.63 | 50 | 78.9 | 43.2 | 77.7 | 44.4 | 218.4 | 219.3 | 218.4 | YES
61 | OK | 112 | 113 | 121 | 45 | 61.7 | 1.81 | 50 | 78.9 | 43.2 | 77.6 | 44.6 | 218.2 | 219.6 | 218.2 | YES
62 | OK | 112 | 114 | 111 | 5 | 30.8 | 6.29 | 50 | 78.9 | 43.2 | 74.3 | 47.9 | 218.5 | 218.7 | 218.5 | YES
63 | OK | 31 | 11 | 11 | 65 | 97.5 | 11.63 | 50 | 78.9 | 43.2 | 70.2 | 51.7 | 219.2 | 219 | 219 | YES
64 | OK | 31 | 48 | 96 | 65 | 20.1 | 10.66 | 50 | 78.9 | 43.2 | 71 | 51 | 218.4 | 219.7 | 218.4 | YES
65 | OK | 117 | 116 | 125 | 82 | 4.5 | 3.43 | 95 | 78.9 | 43.2 | 76.4 | 45.7 | 218.1 | 219.8 | 218.1 | YES
66 | OK | 126 | 123 | 124 | 9 | 29.8 | 1.23 | 50 | 78.9 | 43.2 | 78 | 44.1 | 218.3 | 219.4 | 218.3 | YES
67 | OK | 113 | 121 | 121 | 45 | 61.7 | 1.42 | 50 | 78.9 | 43.2 | 77.9 | 44.3 | 218.2 | 219.7 | 218.2 | YES
68 | OK | 114 | 110 | 111 | 5 | 30.8 | 5.72 | 50 | 78.9 | 43.2 | 74.7 | 47.5 | 218.5 | 218.6 | 218.5 | YES
69 | OK | 11 | 10 | 10 | 65 | 108.9 | 2.26 | 50 | 78.9 | 43.2 | 74.9 | 44.8 | 218.4 | 219.6 | 218.4 | YES
70 | ** OPTIMAL ** | 11 | 9 | 9 | 65 | 122.1 | 7.53 | 50 | 78.9 | 43.2 | 73.3 | 43.2 | 219.2 | 219.8 | 219.2 | YES
71 | OK | 48 | 49 | 96 | 65 | 20.1 | 9.44 | 50 | 78.9 | 43.2 | 71.9 | 50.1 | 218.5 | 219.7 | 218.5 | YES
72 | OK | 116 | 125 | 125 | 82 | 4.5 | 2.67 | 95 | 78.9 | 43.2 | 76.9 | 45.1 | 218.1 | 219.8 | 218.1 | YES
73 | OK | 123 | 124 | 124 | 9 | 29.8 | 0.4 | 50 | 78.9 | 43.2 | 78.7 | 43.5 | 218.2 | 219.7 | 218.2 | YES
74 | OK | 110 | 111 | 111 | 5 | 30.8 | 4.07 | 50 | 78.9 | 43.2 | 75.9 | 46.3 | 218.5 | 218.6 | 218.5 | YES
75 | OK | 110 | 115 | 115 | 43 | 42.3 | 1.65 | 50 | 78.9 | 43.2 | 77.7 | 44.4 | 218.1 | 219.8 | 218.1 | YES
76 | OK | 9 | 33 | 33 | 65 | 140.8 | 3.38 | 50 | 78.9 | 43.2 | 76.4 | 45.7 | 218.6 | 219.7 | 218.6 | YES
77 | OK | 49 | 64 | 96 | 65 | 20.1 | 8.05 | 50 | 78.9 | 43.2 | 72.9 | 49.1 | 218.3 | 219.7 | 218.3 | YES
78 | OK | 115 | 122 | 122 | 45 | 48 | 0.39 | 50 | 78.9 | 43.2 | 78.7 | 43.5 | 218.2 | 219.8 | 218.2 | YES
| NG | 64 | 66 | 66 | 65 | 91.7 | 2.64 | 50 | 78.9 | 43.2 | [5 empty] | NO | TR_A sim: loading 14665% (degenerate)
79 | OK | 64 | 85 | 96 | 65 | 20.1 | 2.81 | 50 | 78.9 | 43.2 | 76.8 | 45.3 | 218 | 219.8 | 218 | YES
| NG | 64 | 90 | 90 | 65 | 106.4 | 2.6 | 50 | 78.9 | 43.2 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 43.2% (degenerate)
| NG | 66 | 67 | 67 | 65 | 96.8 | 1.59 | 50 | 78.9 | 43.2 | 159.6 | 44.4 | 51 | 219.8 | 51 | NO
80 | OK | 85 | 94 | 96 | 65 | 20.1 | 1.42 | 50 | 78.9 | 43.2 | 77.9 | 44.2 | 218.1 | 219.8 | 218.1 | YES
81 | OK | 90 | 84 | 84 | 65 | 128.8 | 0.53 | 50 | 78.9 | 43.2 | 78.5 | 43.6 | 218.8 | 219.8 | 218.8 | YES
82 | OK | 67 | 68 | 68 | 65 | 101 | 0.45 | 50 | 78.9 | 43.2 | 78.5 | 43.5 | 218.8 | 219.8 | 218.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 44-000345
TR_B (available) | 65-006634
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 78.9
TR_B Baseline Loading% | 43.2
Total Scenarios Evaluated | 92
Feasible Scenarios | 82
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 9
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 65
Tie Line Distance (m) | 122.1
Load Transferred (kW) | 7.53
TR_A Loading After (%) | 73.3
TR_B Loading After (%) | 43.2
Minimum Voltage (V) | 219.2