## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 19 | 104 | 24 | 148.6 | 32.96 | 50 | 89.6 | 3.3 | 51.3 | 10.8 | 202.5 | 216.5 | 202.5 | NO
1 | ** OPTIMAL ** | 18 | 114 | 100 | 11 | 9.8 | 33.35 | 50 | 89.6 | 3.3 | 48.7 | 4.5 | 222.6 | 229.2 | 222.6 | YES
| NG | 19 | 64 | 64 | 10 | 167.9 | 10.05 | 50 | 89.6 | 3.3 | 77.5 | 4.7 | 200.4 | 228 | 200.4 | NO
| NG | 19 | 17 | 17 | 10 | 164.2 | 21.63 | 50 | 89.6 | 3.3 | 64.4 | 8.4 | 201.3 | 218.1 | 201.3 | NO
2 | OK | 114 | 61 | 85 | 22 | 86.8 | 28.74 | 50 | 89.6 | 3.3 | 54 | 3.3 | 222.4 | 229.4 | 222.4 | YES
| NG | 17 | 16 | 16 | 10 | 169.7 | 21.63 | 50 | 89.6 | 3.3 | 64.4 | 8.4 | 201.3 | 218.1 | 201.3 | NO
3 | OK | 61 | 80 | 95 | 22 | 87.3 | 25.49 | 50 | 89.6 | 3.3 | 57.7 | 3.3 | 222.2 | 229.4 | 222.2 | YES
4 | OK | 80 | 81 | 81 | 14 | 98.4 | 21.63 | 50 | 89.6 | 3.3 | 61 | 3.3 | 222.2 | 229.4 | 222.2 | YES
5 | OK | 81 | 87 | 87 | 14 | 99.2 | 21.63 | 50 | 89.6 | 3.3 | 61 | 3.3 | 222.2 | 229.4 | 222.2 | YES
6 | OK | 87 | 89 | 89 | 14 | 101.9 | 21.61 | 50 | 89.6 | 3.3 | 61.1 | 3.3 | 222.2 | 229.4 | 222.2 | YES
7 | OK | 89 | 68 | 68 | 14 | 125.5 | 15.89 | 50 | 89.6 | 3.3 | 69 | 3.3 | 219.7 | 229.4 | 219.7 | YES
8 | OK | 68 | 69 | 69 | 14 | 162.5 | 15.63 | 50 | 89.6 | 3.3 | 69.3 | 3.3 | 219.7 | 229.4 | 219.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 44-005019
TR_B (available) | 60-037278
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 89.6
TR_B Baseline Loading% | 3.3
Total Scenarios Evaluated | 12
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 18
Switch Child Node | 114
Tie Node (TR_A side) | 100
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 9.8
Load Transferred (kW) | 33.35
TR_A Loading After (%) | 48.7
TR_B Loading After (%) | 4.5
Minimum Voltage (V) | 222.6