## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 20 | 19 | 5 | 32 | 6.1 | 11.84 | 50 | 80.5 | 37.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 20 | 22 | 38 | 45 | 24.7 | 9.13 | 50 | 80.5 | 37.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 19 | 12 | 5 | 32 | 6.1 | 11.23 | 50 | 80.5 | 37.6 | 37.3 | 65 | 224.4 | 208.5 | 208.5 | NO
1 | OK | 19 | 21 | 21 | 32 | 58.1 | 0.61 | 50 | 80.5 | 37.6 | 78.1 | 39 | 218.4 | 221.9 | 218.4 | YES
2 | OK | 22 | 23 | 38 | 45 | 24.7 | 7.22 | 50 | 80.5 | 37.6 | 52.7 | 45.5 | 221.4 | 219.4 | 219.4 | YES
3 | OK | 12 | 13 | 16 | 33 | 33.9 | 1.27 | 50 | 80.5 | 37.6 | 75.6 | 40.6 | 218.4 | 222 | 218.4 | YES
| NG | 12 | 15 | 5 | 32 | 6.1 | 9.96 | 50 | 80.5 | 37.6 | 42.2 | 61.9 | 224.4 | 208 | 208 | NO
4 | OK | 21 | 18 | 18 | 32 | 74 | 0.18 | 50 | 80.5 | 37.6 | 79.8 | 38 | 218.4 | 221.7 | 218.4 | YES
5 | OK | 23 | 24 | 38 | 45 | 24.7 | 7.07 | 50 | 80.5 | 37.6 | 53.3 | 45.2 | 221.4 | 219.7 | 219.7 | YES
| NG | 13 | 16 | 16 | 33 | 33.9 | 0.56 | 50 | 80.5 | 37.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 37.6% (degenerate)
| NG | 15 | 14 | 5 | 32 | 6.1 | 7.85 | 50 | 80.5 | 37.6 | 50.2 | 56.7 | 223.8 | 209.1 | 209.1 | NO
6 | OK | 24 | 25 | 25 | 32 | 115.4 | 1.65 | 50 | 80.5 | 37.6 | 74.1 | 41.5 | 218.4 | 222.1 | 218.4 | YES
7 | OK | 24 | 26 | 26 | 45 | 102.2 | 5.22 | 50 | 80.5 | 37.6 | 60.4 | 40.8 | 221.4 | 221.9 | 221.4 | YES
8 | OK | 24 | 36 | 38 | 45 | 24.7 | 0.2 | 50 | 80.5 | 37.6 | 79.7 | 38.1 | 218.4 | 221.7 | 218.4 | YES
| NG | 14 | 5 | 5 | 32 | 6.1 | 7.44 | 50 | 80.5 | 37.6 | 51.8 | 55.7 | 223.7 | 209.6 | 209.6 | NO
9 | OK | 25 | 1 | 1 | 32 | 126.4 | 0.98 | 50 | 80.5 | 37.6 | 76.7 | 39.9 | 218.4 | 222 | 218.4 | YES
10 | OK | 26 | 27 | 27 | 45 | 108.4 | 3.87 | 50 | 80.5 | 37.6 | 65.5 | 40.5 | 220.4 | 221.9 | 220.4 | YES
11 | OK | 5 | 4 | 4 | 32 | 7 | 3.87 | 50 | 80.5 | 37.6 | 63.6 | 47.2 | 222.6 | 211.3 | 211.3 | YES
12 | OK | 5 | 6 | 6 | 32 | 42.5 | 3.07 | 50 | 80.5 | 37.6 | 68.7 | 44.8 | 218.9 | 221 | 218.9 | YES
13 | OK | 1 | 0 | 0 | 32 | 168.3 | 0.21 | 50 | 80.5 | 37.6 | 79.6 | 38.1 | 218.4 | 221.7 | 218.4 | YES
14 | OK | 27 | 28 | 28 | 45 | 121.4 | 0.4 | 50 | 80.5 | 37.6 | 78.9 | 38.5 | 218.4 | 221.7 | 218.4 | YES
15 | OK | 27 | 29 | 29 | 45 | 110.7 | 3.47 | 50 | 80.5 | 37.6 | 67.1 | 39.6 | 220.4 | 221.8 | 220.4 | YES
16 | OK | 4 | 39 | 39 | 32 | 43.4 | 3.63 | 50 | 80.5 | 37.6 | 66.4 | 46.6 | 222.7 | 211.8 | 211.8 | YES
17 | OK | 6 | 47 | 47 | 32 | 86.2 | 2.12 | 50 | 80.5 | 37.6 | 72.3 | 42.6 | 218.8 | 221.2 | 218.8 | YES
18 | OK | 28 | 30 | 30 | 45 | 158.5 | 0.23 | 50 | 80.5 | 37.6 | 79.6 | 38.1 | 218.4 | 221.7 | 218.4 | YES
19 | OK | 29 | 32 | 32 | 45 | 119.9 | 3.47 | 50 | 80.5 | 37.6 | 67.1 | 39.6 | 220.4 | 221.8 | 220.4 | YES
20 | ** OPTIMAL ** | 39 | 40 | 3 | 34 | 44.8 | 3.25 | 50 | 80.5 | 37.6 | 67.8 | 38.2 | 222.4 | 221.7 | 221.7 | YES
21 | OK | 47 | 7 | 7 | 32 | 90.9 | 0.92 | 50 | 80.5 | 37.6 | 76.9 | 39.8 | 218.9 | 220.7 | 218.9 | YES
22 | OK | 32 | 33 | 33 | 45 | 143.1 | 1.93 | 50 | 80.5 | 37.6 | 73 | 39.4 | 219.3 | 221.8 | 219.3 | YES
23 | OK | 40 | 2 | 3 | 34 | 44.8 | 0.24 | 50 | 80.5 | 37.6 | 79.5 | 38.2 | 218.4 | 221.7 | 218.4 | YES
24 | OK | 40 | 41 | 41 | 30 | 70.6 | 3.01 | 50 | 80.5 | 37.6 | 68.8 | 45 | 222.4 | 213.8 | 213.8 | YES
25 | OK | 7 | 8 | 8 | 32 | 91.5 | 0.92 | 50 | 80.5 | 37.6 | 76.9 | 39.8 | 218.9 | 220.7 | 218.9 | YES
26 | OK | 33 | 34 | 34 | 45 | 173 | 1.76 | 50 | 80.5 | 37.6 | 73.6 | 39 | 219.3 | 221.8 | 219.3 | YES
27 | OK | 41 | 42 | 42 | 30 | 71 | 3.01 | 50 | 80.5 | 37.6 | 68.8 | 45 | 222.4 | 213.9 | 213.9 | YES
28 | OK | 8 | 9 | 9 | 32 | 102.6 | 0.79 | 50 | 80.5 | 37.6 | 77.4 | 39.5 | 218.9 | 220.7 | 218.9 | YES
29 | OK | 42 | 43 | 43 | 31 | 71.6 | 2.72 | 50 | 80.5 | 37.6 | 69.9 | 44.3 | 222.2 | 214.3 | 214.3 | YES
30 | OK | 9 | 10 | 10 | 32 | 134.6 | 0.32 | 50 | 80.5 | 37.6 | 79.2 | 38.4 | 218.4 | 221.8 | 218.4 | YES
31 | OK | 43 | 44 | 44 | 31 | 106.3 | 2.11 | 50 | 80.5 | 37.6 | 72.2 | 42.8 | 221.7 | 215.9 | 215.9 | YES
| NG | 10 | 11 | 11 | 32 | 136.5 | 0.32 | 50 | 80.5 | 37.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 37.6% (degenerate)
32 | OK | 44 | 49 | 55 | 32 | 122.7 | 1.84 | 50 | 80.5 | 37.6 | 73.3 | 42.1 | 221.5 | 217 | 217 | YES
33 | OK | 44 | 45 | 45 | 31 | 120.6 | 0.27 | 50 | 80.5 | 37.6 | 79.4 | 38.3 | 218.9 | 221.1 | 218.9 | YES
34 | OK | 49 | 50 | 55 | 32 | 122.7 | 1.84 | 50 | 80.5 | 37.6 | 73.3 | 42.1 | 221.5 | 217 | 217 | YES
35 | OK | 45 | 46 | 46 | 31 | 122.9 | 0.27 | 50 | 80.5 | 37.6 | 79.4 | 37.8 | 218.9 | 221.6 | 218.9 | YES
36 | OK | 50 | 52 | 55 | 32 | 122.7 | 1.84 | 50 | 80.5 | 37.6 | 73.3 | 42.1 | 221.5 | 217 | 217 | YES
37 | OK | 52 | 53 | 55 | 32 | 122.7 | 0.9 | 50 | 80.5 | 37.6 | 73.3 | 39.8 | 221.5 | 219.5 | 219.5 | YES
38 | OK | 53 | 54 | 55 | 32 | 122.7 | 0.9 | 50 | 80.5 | 37.6 | 76.9 | 39.8 | 220.6 | 219.5 | 219.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-002508
TR_B (available) | 65-014931
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 80.5
TR_B Baseline Loading% | 37.6
Total Scenarios Evaluated | 46
Feasible Scenarios | 38
--- Optimal Solution ---
Switch Parent Node | 39
Switch Child Node | 40
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 34
Tie Line Distance (m) | 44.8
Load Transferred (kW) | 3.25
TR_A Loading After (%) | 67.8
TR_B Loading After (%) | 38.2
Minimum Voltage (V) | 221.7