## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 12 | 0 | 20 | 150.4 | 12.72 | 50 | 85.7 | 7.4 | 36.6 | 39 | 223.5 | 189.8 | 189.8 | NO
| NG | 12 | 11 | 0 | 20 | 150.4 | 10.9 | 50 | 85.7 | 7.4 | 43.6 | 32.7 | 223 | 198.6 | 198.6 | NO
| NG | 11 | 10 | 0 | 20 | 150.4 | 7.75 | 50 | 85.7 | 7.4 | 55.6 | 25.1 | 221.9 | 208.7 | 208.7 | NO
1 | ** OPTIMAL ** | 10 | 9 | 0 | 20 | 150.4 | 5.25 | 50 | 85.7 | 7.4 | 65.2 | 15.1 | 221.8 | 221.8 | 221.8 | YES
2 | OK | 9 | 8 | 0 | 20 | 150.4 | 5.05 | 50 | 85.7 | 7.4 | 66 | 15.1 | 221.6 | 221.8 | 221.6 | YES
3 | OK | 8 | 7 | 0 | 20 | 150.4 | 4.71 | 50 | 85.7 | 7.4 | 67.3 | 14.5 | 221.5 | 222.6 | 221.5 | YES
4 | OK | 7 | 6 | 0 | 20 | 150.4 | 3.88 | 50 | 85.7 | 7.4 | 70.5 | 13.5 | 221 | 223.4 | 221 | YES
5 | OK | 6 | 25 | 0 | 20 | 150.4 | 3.88 | 50 | 85.7 | 7.4 | 70.5 | 13.5 | 221 | 223.4 | 221 | YES
6 | OK | 25 | 5 | 0 | 20 | 150.4 | 3.65 | 50 | 85.7 | 7.4 | 71.4 | 13.5 | 220.9 | 223.4 | 220.9 | YES
7 | OK | 5 | 4 | 0 | 20 | 150.4 | 2.45 | 50 | 85.7 | 7.4 | 76.1 | 13.5 | 218.8 | 223.4 | 218.8 | YES
8 | OK | 4 | 3 | 0 | 20 | 150.4 | 2.32 | 50 | 85.7 | 7.4 | 76.6 | 13 | 218.8 | 223.5 | 218.8 | YES
9 | OK | 3 | 2 | 0 | 20 | 150.4 | 2.24 | 50 | 85.7 | 7.4 | 76.9 | 13 | 218.7 | 223.5 | 218.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-002745
TR_B (available) | 63-019593
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.7
TR_B Baseline Loading% | 7.4
Total Scenarios Evaluated | 12
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 9
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 20
Tie Line Distance (m) | 150.4
Load Transferred (kW) | 5.25
TR_A Loading After (%) | 65.2
TR_B Loading After (%) | 15.1
Minimum Voltage (V) | 221.8