## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 65 | 10 | 54 | 8.7 | 23.55 | 95 | 58.2 | 42.8 | 3.4 | 60.9 | 230 | 208.7 | 208.7 | NO
1 | OK | 65 | 36 | 10 | 54 | 8.7 | 22.32 | 95 | 58.2 | 42.8 | 6.2 | 59.9 | 229.5 | 210.8 | 210.8 | YES
| NG | 36 | 58 | 10 | 54 | 8.7 | 16.16 | 95 | 58.2 | 42.8 | 20.5 | 55.2 | 223.2 | 209 | 209 | NO
| NG | 58 | 33 | 10 | 54 | 8.7 | 16.16 | 95 | 58.2 | 42.8 | 20.5 | 55.2 | 223.2 | 209 | 209 | NO
| NG | 33 | 19 | 10 | 54 | 8.7 | 16.16 | 95 | 58.2 | 42.8 | 20.5 | 55.2 | 223.2 | 209 | 209 | NO
| NG | 19 | 20 | 10 | 54 | 8.7 | 16.16 | 95 | 58.2 | 42.8 | 20.5 | 55.2 | 223.2 | 209 | 209 | NO
| NG | 20 | 21 | 10 | 54 | 8.7 | 16.16 | 95 | 58.2 | 42.8 | 20.5 | 55.2 | 223.2 | 209 | 209 | NO
| NG | 21 | 18 | 10 | 54 | 8.7 | 14.8 | 95 | 58.2 | 42.8 | 23.7 | 54.2 | 223.2 | 209 | 209 | NO
2 | OK | 18 | 35 | 63 | 59 | 127.4 | 2.43 | 50 | 58.2 | 42.8 | 52.6 | 44.7 | 218.8 | 220.6 | 218.8 | YES
| NG | 18 | 3 | 10 | 54 | 8.7 | 11.68 | 95 | 58.2 | 42.8 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 42.8% (degenerate)
3 | OK | 35 | 63 | 63 | 59 | 127.4 | 1.65 | 50 | 58.2 | 42.8 | 54.4 | 44.1 | 218.1 | 221 | 218.1 | YES
4 | OK | 3 | 4 | 10 | 54 | 8.7 | 11.07 | 95 | 58.2 | 42.8 | 32.2 | 51.3 | 222.6 | 210.2 | 210.2 | YES
| NG | 4 | 27 | 10 | 54 | 8.7 | 10.63 | 95 | 58.2 | 42.8 | 33.2 | 50.8 | 222.4 | 209.9 | 209.9 | NO
| NG | 27 | 14 | 10 | 54 | 8.7 | 10.32 | 95 | 58.2 | 42.8 | 33.9 | 50.8 | 222.2 | 209.9 | 209.9 | NO
5 | OK | 14 | 15 | 17 | 26 | 32 | 4.56 | 50 | 58.2 | 42.8 | 47.3 | 46.4 | 221.7 | 213.7 | 213.7 | YES
6 | OK | 14 | 24 | 60 | 97 | 50.4 | 4.6 | 50 | 58.2 | 42.8 | 47.3 | 46.3 | 221.7 | 217.1 | 217.1 | YES
7 | OK | 14 | 12 | 10 | 54 | 8.7 | 0.98 | 95 | 58.2 | 42.8 | 55.5 | 43.5 | 218.1 | 221.1 | 218.1 | YES
8 | OK | 15 | 61 | 17 | 26 | 32 | 4.18 | 50 | 58.2 | 42.8 | 48.2 | 46.1 | 221.7 | 214.5 | 214.5 | YES
9 | OK | 24 | 5 | 60 | 97 | 50.4 | 1.95 | 50 | 58.2 | 42.8 | 53.5 | 44.3 | 220 | 221.1 | 220 | YES
10 | OK | 12 | 9 | 10 | 54 | 8.7 | 0.98 | 95 | 58.2 | 42.8 | 55.9 | 43.5 | 218.1 | 221.1 | 218.1 | YES
11 | OK | 61 | 22 | 17 | 26 | 32 | 4.04 | 50 | 58.2 | 42.8 | 48.5 | 45.9 | 221.7 | 214.9 | 214.9 | YES
12 | OK | 5 | 6 | 6 | 54 | 83.1 | 1.56 | 50 | 58.2 | 42.8 | 54.5 | 44 | 219.6 | 220.9 | 219.6 | YES
13 | OK | 5 | 25 | 60 | 97 | 50.4 | 0.39 | 50 | 58.2 | 42.8 | 57.3 | 43.1 | 218.4 | 221.1 | 218.4 | YES
14 | OK | 22 | 23 | 32 | 56 | 60.9 | 3.15 | 50 | 58.2 | 42.8 | 50.6 | 45.2 | 221.7 | 217.9 | 217.9 | YES
15 | OK | 22 | 13 | 17 | 26 | 32 | 0.74 | 50 | 58.2 | 42.8 | 56.4 | 43.4 | 219.1 | 220.8 | 219.1 | YES
16 | OK | 6 | 11 | 8 | 103 | 98.2 | 1.13 | 50 | 58.2 | 42.8 | 55.5 | 42.9 | 219.1 | 221.1 | 219.1 | YES
17 | OK | 25 | 26 | 60 | 97 | 50.4 | 0.39 | 50 | 58.2 | 42.8 | 57.3 | 43.1 | 218.4 | 221.1 | 218.4 | YES
18 | OK | 23 | 29 | 32 | 56 | 60.9 | 1.97 | 50 | 58.2 | 42.8 | 53.4 | 44.3 | 221.5 | 219.6 | 219.6 | YES
19 | OK | 13 | 28 | 17 | 26 | 32 | 0.22 | 50 | 58.2 | 42.8 | 57.7 | 43 | 218.3 | 221 | 218.3 | YES
20 | OK | 11 | 7 | 8 | 103 | 98.2 | 0.6 | 50 | 58.2 | 42.8 | 55.7 | 42.8 | 219.1 | 221.1 | 219.1 | YES
21 | OK | 29 | 30 | 30 | 54 | 87.8 | 0.13 | 50 | 58.2 | 42.8 | 57.9 | 42.9 | 218.2 | 221.1 | 218.2 | YES
22 | OK | 29 | 31 | 31 | 30 | 68.7 | 0.26 | 50 | 58.2 | 42.8 | 57.6 | 43 | 218.4 | 221 | 218.4 | YES
23 | ** OPTIMAL ** | 29 | 32 | 32 | 56 | 60.9 | 1.58 | 50 | 58.2 | 42.8 | 54.4 | 44 | 220.8 | 220.2 | 220.2 | YES
24 | OK | 28 | 16 | 17 | 26 | 32 | 0.17 | 50 | 58.2 | 42.8 | 57.8 | 42.9 | 218.2 | 221 | 218.2 | YES
25 | OK | 7 | 8 | 8 | 103 | 98.2 | 0.01 | 50 | 58.2 | 42.8 | 58.2 | 42.8 | 218 | 221.1 | 218 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-003402
TR_B (available) | 24-011662
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 58.2
TR_B Baseline Loading% | 42.8
Total Scenarios Evaluated | 35
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 32
Tie Node (TR_A side) | 32
Tie Node (TR_B side) | 56
Tie Line Distance (m) | 60.9
Load Transferred (kW) | 1.58
TR_A Loading After (%) | 54.4
TR_B Loading After (%) | 44
Minimum Voltage (V) | 220.2