## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 0 | 65 | 65 | 5 | 83.2 | 23.55 | 50 | 58.2 | 10.9 | 3.4 | 66.9 | 230 | 211.3 | 211.3 | YES
2 | OK | 0 | 2 | 1 | 3 | 15.5 | 1.5 | 50 | 58.2 | 10.9 | 54.8 | 14.4 | 217.9 | 228.5 | 217.9 | YES
3 | OK | 65 | 36 | 36 | 5 | 106.2 | 22.32 | 50 | 58.2 | 10.9 | 6.2 | 64 | 229.5 | 210.8 | 210.8 | YES
4 | ** OPTIMAL ** | 2 | 1 | 1 | 3 | 15.5 | 0.51 | 50 | 58.2 | 10.9 | 57.1 | 12.1 | 217.9 | 228.5 | 217.9 | YES
| NG | 36 | 58 | 58 | 5 | 110.4 | 16.16 | 50 | 58.2 | 10.9 | 20.5 | 49.5 | 223.2 | 209.9 | 209.9 | NO
| NG | 58 | 33 | 33 | 5 | 114 | 16.16 | 50 | 58.2 | 10.9 | 20.5 | 49.5 | 223.2 | 209.8 | 209.8 | NO
| NG | 33 | 19 | 19 | 5 | 119.8 | 16.16 | 50 | 58.2 | 10.9 | 20.5 | 49.5 | 223.2 | 209.7 | 209.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 45-003402
TR_B (available) | 40-023022
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 58.2
TR_B Baseline Loading% | 10.9
Total Scenarios Evaluated | 7
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 1
Tie Node (TR_A side) | 1
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 15.5
Load Transferred (kW) | 0.51
TR_A Loading After (%) | 57.1
TR_B Loading After (%) | 12.1
Minimum Voltage (V) | 217.9