## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 65 | 63 | 48 | 42.2 | 23.55 | 50 | 58.2 | 18.4 | 3.4 | 37.1 | 230 | 199.4 | 199.4 | NO
| NG | 65 | 36 | 63 | 48 | 42.2 | 22.32 | 50 | 58.2 | 18.4 | 6.2 | 36 | 229.5 | 198.5 | 198.5 | NO
| NG | 36 | 58 | 63 | 48 | 42.2 | 16.16 | 50 | 58.2 | 18.4 | 20.5 | 31.3 | 223.2 | 194.6 | 194.6 | NO
| NG | 58 | 33 | 63 | 48 | 42.2 | 16.16 | 50 | 58.2 | 18.4 | 20.5 | 31.3 | 223.2 | 194.6 | 194.6 | NO
| NG | 33 | 19 | 63 | 48 | 42.2 | 16.16 | 50 | 58.2 | 18.4 | 20.5 | 31.3 | 223.2 | 194.6 | 194.6 | NO
| NG | 19 | 20 | 63 | 48 | 42.2 | 16.16 | 50 | 58.2 | 18.4 | 20.5 | 31.3 | 223.2 | 194.6 | 194.6 | NO
| NG | 20 | 21 | 63 | 48 | 42.2 | 16.16 | 50 | 58.2 | 18.4 | 20.5 | 31.3 | 223.2 | 194.6 | 194.6 | NO
| NG | 21 | 18 | 63 | 48 | 42.2 | 14.8 | 50 | 58.2 | 18.4 | 23.7 | 30.3 | 223.2 | 194.4 | 194.4 | NO
1 | OK | 18 | 35 | 63 | 48 | 42.2 | 2.43 | 50 | 58.2 | 18.4 | 52.6 | 20.1 | 218.8 | 225.5 | 218.8 | YES
| NG | 18 | 3 | 13 | 48 | 87.1 | 11.68 | 50 | 58.2 | 18.4 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 18.4% (degenerate)
2 | OK | 35 | 63 | 63 | 48 | 42.2 | 1.65 | 50 | 58.2 | 18.4 | 54.4 | 19.6 | 218.1 | 225 | 218.1 | YES
| NG | 3 | 4 | 13 | 48 | 87.1 | 11.07 | 50 | 58.2 | 18.4 | 32.2 | 27.3 | 222.6 | 198.5 | 198.5 | NO
| NG | 4 | 27 | 13 | 48 | 87.1 | 10.63 | 50 | 58.2 | 18.4 | 33.2 | 26.8 | 222.4 | 197.8 | 197.8 | NO
| NG | 27 | 14 | 13 | 48 | 87.1 | 10.32 | 50 | 58.2 | 18.4 | 33.9 | 26.8 | 222.2 | 197.8 | 197.8 | NO
3 | OK | 14 | 15 | 13 | 48 | 87.1 | 4.56 | 50 | 58.2 | 18.4 | 47.3 | 21.9 | 221.7 | 215.5 | 215.5 | YES
4 | OK | 14 | 12 | 12 | 48 | 133.4 | 0.98 | 95 | 58.2 | 18.4 | 55.5 | 19.1 | 218.1 | 226.7 | 218.1 | YES
5 | OK | 15 | 61 | 13 | 48 | 87.1 | 4.18 | 50 | 58.2 | 18.4 | 48.2 | 21.5 | 221.7 | 216.6 | 216.6 | YES
6 | OK | 12 | 9 | 9 | 48 | 148.8 | 0.98 | 95 | 58.2 | 18.4 | 55.9 | 19.1 | 218.1 | 226.7 | 218.1 | YES
7 | OK | 61 | 22 | 13 | 48 | 87.1 | 4.04 | 50 | 58.2 | 18.4 | 48.5 | 21.4 | 221.7 | 217 | 217 | YES
8 | OK | 22 | 23 | 23 | 48 | 135.8 | 3.15 | 50 | 58.2 | 18.4 | 50.6 | 20.7 | 221.7 | 220.1 | 220.1 | YES
9 | OK | 22 | 13 | 13 | 48 | 87.1 | 0.74 | 50 | 58.2 | 18.4 | 56.4 | 18.9 | 219.1 | 226.5 | 219.1 | YES
10 | ** OPTIMAL ** | 23 | 29 | 30 | 48 | 145.9 | 1.97 | 50 | 58.2 | 18.4 | 53.4 | 19.8 | 221.5 | 223.1 | 221.5 | YES
11 | OK | 13 | 28 | 28 | 48 | 97.7 | 0.22 | 50 | 58.2 | 18.4 | 57.7 | 18.5 | 218.3 | 226.7 | 218.3 | YES
12 | OK | 29 | 30 | 30 | 48 | 145.9 | 0.13 | 50 | 58.2 | 18.4 | 57.9 | 18.5 | 218.2 | 226.6 | 218.2 | YES
13 | OK | 29 | 32 | 32 | 48 | 148.6 | 1.58 | 50 | 58.2 | 18.4 | 54.4 | 19.5 | 220.8 | 224.3 | 220.8 | YES
14 | OK | 28 | 16 | 16 | 48 | 138.4 | 0.17 | 50 | 58.2 | 18.4 | 57.8 | 18.5 | 218.2 | 226.6 | 218.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-003402
TR_B (available) | 45-010415
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 58.2
TR_B Baseline Loading% | 18.4
Total Scenarios Evaluated | 26
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 29
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 48
Tie Line Distance (m) | 145.9
Load Transferred (kW) | 1.97
TR_A Loading After (%) | 53.4
TR_B Loading After (%) | 19.8
Minimum Voltage (V) | 221.5