## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 65 | 8 | 73 | 78 | 23.55 | 50 | 58.2 | 31.5 | 3.4 | 50.5 | 230 | 197 | 197 | NO
| NG | 65 | 36 | 8 | 73 | 78 | 22.32 | 50 | 58.2 | 31.5 | 6.2 | 49.4 | 229.5 | 196.2 | 196.2 | NO
| NG | 36 | 58 | 8 | 73 | 78 | 16.16 | 50 | 58.2 | 31.5 | 20.5 | 44.5 | 223.2 | 192.2 | 192.2 | NO
| NG | 58 | 33 | 8 | 73 | 78 | 16.16 | 50 | 58.2 | 31.5 | 20.5 | 44.5 | 223.2 | 192.2 | 192.2 | NO
| NG | 33 | 19 | 8 | 73 | 78 | 16.16 | 50 | 58.2 | 31.5 | 20.5 | 44.5 | 223.2 | 192.2 | 192.2 | NO
| NG | 19 | 20 | 8 | 73 | 78 | 16.16 | 50 | 58.2 | 31.5 | 20.5 | 44.5 | 223.2 | 192.2 | 192.2 | NO
| NG | 20 | 21 | 8 | 73 | 78 | 16.16 | 50 | 58.2 | 31.5 | 20.5 | 44.5 | 223.2 | 192.2 | 192.2 | NO
| NG | 21 | 18 | 8 | 73 | 78 | 14.8 | 50 | 58.2 | 31.5 | 23.7 | 43.5 | 223.2 | 191.9 | 191.9 | NO
| NG | 18 | 3 | 8 | 73 | 78 | 11.68 | 50 | 58.2 | 31.5 | 30.8 | 23 | 223 | 5.5 | 5.5 | NO
| NG | 3 | 4 | 8 | 73 | 78 | 11.07 | 50 | 58.2 | 31.5 | 32.2 | 40.6 | 222.6 | 195 | 195 | NO
| NG | 4 | 27 | 8 | 73 | 78 | 10.63 | 50 | 58.2 | 31.5 | 33.2 | 40 | 222.4 | 194.4 | 194.4 | NO
| NG | 27 | 14 | 8 | 73 | 78 | 10.32 | 50 | 58.2 | 31.5 | 33.9 | 40 | 222.2 | 194.4 | 194.4 | NO
1 | OK | 14 | 24 | 8 | 73 | 78 | 4.6 | 50 | 58.2 | 31.5 | 47.3 | 35.1 | 221.7 | 214.3 | 214.3 | YES
2 | ** OPTIMAL ** | 24 | 5 | 8 | 73 | 78 | 1.95 | 50 | 58.2 | 31.5 | 53.5 | 33 | 220 | 216.2 | 216.2 | YES
3 | OK | 5 | 6 | 8 | 73 | 78 | 1.56 | 50 | 58.2 | 31.5 | 54.5 | 32.7 | 219.6 | 216.2 | 216.2 | YES
4 | OK | 5 | 25 | 60 | 24 | 127.5 | 0.39 | 50 | 58.2 | 31.5 | 57.3 | 31.8 | 218.4 | 216.2 | 216.2 | YES
5 | OK | 6 | 11 | 8 | 73 | 78 | 1.13 | 50 | 58.2 | 31.5 | 55.5 | 32.4 | 219.1 | 216.2 | 216.2 | YES
6 | OK | 25 | 26 | 60 | 24 | 127.5 | 0.39 | 50 | 58.2 | 31.5 | 57.3 | 31.8 | 218.4 | 216.2 | 216.2 | YES
7 | OK | 11 | 7 | 8 | 73 | 78 | 0.6 | 50 | 58.2 | 31.5 | 55.7 | 32 | 219.1 | 216.2 | 216.2 | YES
8 | OK | 7 | 8 | 8 | 73 | 78 | 0.01 | 50 | 58.2 | 31.5 | 58.2 | 31.6 | 218 | 216.2 | 216.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-003402
TR_B (available) | 45-015482
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 58.2
TR_B Baseline Loading% | 31.5
Total Scenarios Evaluated | 20
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 5
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 73
Tie Line Distance (m) | 78
Load Transferred (kW) | 1.95
TR_A Loading After (%) | 53.5
TR_B Loading After (%) | 33
Minimum Voltage (V) | 216.2