## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 44 | 46 | 57 | 17 | 31.7 | 1.47 | 50 | 58.2 | 72.5 | 54.8 | 72.5 | 217.9 | 215 | 215 | YES
2 | OK | 46 | 47 | 57 | 17 | 31.7 | 1.47 | 50 | 58.2 | 72.5 | 54.8 | 72.5 | 217.9 | 215 | 215 | YES
| NG | 64 | 42 | 40 | 5 | 178.4 | 2.12 | 50 | 58.2 | 72.5 | 53.2 | 80.7 | 217.9 | 215 | 215 | NO
3 | OK | 47 | 67 | 57 | 17 | 31.7 | 1.39 | 50 | 58.2 | 72.5 | 55 | 72.5 | 217.9 | 215 | 215 | YES
4 | OK | 21 | 53 | 66 | 17 | 146.9 | 1.36 | 50 | 58.2 | 72.5 | 55.1 | 77.9 | 217.9 | 213.3 | 213.3 | YES
5 | ** OPTIMAL ** | 42 | 43 | 40 | 5 | 178.4 | 1.62 | 50 | 58.2 | 72.5 | 54.4 | 78.7 | 217.9 | 215 | 215 | YES
6 | OK | 67 | 48 | 57 | 17 | 31.7 | 1.39 | 50 | 58.2 | 72.5 | 55 | 72.5 | 217.9 | 215 | 215 | YES
7 | OK | 53 | 54 | 66 | 17 | 146.9 | 1.05 | 50 | 58.2 | 72.5 | 55.8 | 76.7 | 217.9 | 213.7 | 213.7 | YES
8 | OK | 43 | 40 | 40 | 5 | 178.4 | 0.78 | 50 | 58.2 | 72.5 | 56.4 | 75.5 | 217.9 | 215 | 215 | YES
9 | OK | 48 | 49 | 57 | 17 | 31.7 | 1.39 | 50 | 58.2 | 72.5 | 55 | 72.5 | 217.9 | 215 | 215 | YES
10 | OK | 54 | 59 | 66 | 17 | 146.9 | 1.04 | 50 | 58.2 | 72.5 | 55.8 | 76.6 | 217.9 | 213.7 | 213.7 | YES
11 | OK | 49 | 50 | 57 | 17 | 31.7 | 1.39 | 50 | 58.2 | 72.5 | 55 | 72.5 | 217.9 | 215 | 215 | YES
12 | OK | 59 | 55 | 66 | 17 | 146.9 | 1.01 | 50 | 58.2 | 72.5 | 55.9 | 76.5 | 217.9 | 213.8 | 213.8 | YES
13 | OK | 50 | 56 | 57 | 17 | 31.7 | 0.17 | 50 | 58.2 | 72.5 | 57.8 | 72.5 | 217.9 | 215 | 215 | YES
14 | OK | 55 | 51 | 66 | 17 | 146.9 | 1.01 | 50 | 58.2 | 72.5 | 55.9 | 76.5 | 217.9 | 213.8 | 213.8 | YES
15 | OK | 51 | 52 | 66 | 17 | 146.9 | 0.18 | 50 | 58.2 | 72.5 | 57.8 | 73.2 | 217.9 | 214.7 | 214.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-003402
TR_B (available) | 54-011038
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 58.2
TR_B Baseline Loading% | 72.5
Total Scenarios Evaluated | 16
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 42
Switch Child Node | 43
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 178.4
Load Transferred (kW) | 1.62
TR_A Loading After (%) | 54.4
TR_B Loading After (%) | 78.7
Minimum Voltage (V) | 215