## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 40 | 13 | 4 | 26 | 66.8 | 29.59 | 50 | 89.4 | 44.4 | 54.4 | 52 | 209.7 | 204.2 | 204.2 | NO
| NG | 13 | 6 | 4 | 26 | 66.8 | 28.12 | 50 | 89.4 | 44.4 | 56.1 | 52 | 209.7 | 204.2 | 204.2 | NO
| NG | 106 | 105 | 108 | 26 | 3.1 | 15.27 | 50 | 89.4 | 44.4 | 71.8 | 68.4 | 206 | 164.3 | 164.3 | NO
1 | ** OPTIMAL ** | 106 | 130 | 130 | 26 | 104.1 | 24.9 | 50 | 89.4 | 44.4 | 59.8 | 48.5 | 214.6 | 214.8 | 214.6 | YES
| NG | 6 | 7 | 7 | 26 | 71.6 | 25.04 | 50 | 89.4 | 44.4 | 59.6 | 51 | 209.7 | 206.7 | 206.7 | NO
| NG | 105 | 84 | 108 | 26 | 3.1 | 15.27 | 50 | 89.4 | 44.4 | 71.8 | 68.4 | 206 | 164.3 | 164.3 | NO
| NG | 130 | 129 | 117 | 29 | 142.5 | 24.9 | 50 | 89.4 | 44.4 | [5 empty] | NO | TR_B sim: not converged
| NG | 7 | 58 | 58 | 26 | 98.9 | 25.04 | 50 | 89.4 | 44.4 | 59.6 | 51 | 209.7 | 206.7 | 206.7 | NO
| NG | 84 | 74 | 108 | 26 | 3.1 | 14.12 | 50 | 89.4 | 44.4 | 72.9 | 65.7 | 208.1 | 171.4 | 171.4 | NO
| NG | 129 | 88 | 117 | 29 | 142.5 | 24.76 | 50 | 89.4 | 44.4 | [5 empty] | NO | TR_B sim: not converged
| NG | 58 | 102 | 31 | 17 | 110.9 | 24.13 | 50 | 89.4 | 44.4 | 60.7 | 73.9 | 209.6 | 204.2 | 204.2 | NO
| NG | 74 | 75 | 108 | 26 | 3.1 | 9.83 | 50 | 89.4 | 44.4 | 77.9 | 57.7 | 207.8 | 192.1 | 192.1 | NO
| NG | 102 | 103 | 31 | 17 | 110.9 | 23.7 | 50 | 89.4 | 44.4 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 44.4% (degenerate)
| NG | 75 | 76 | 108 | 26 | 3.1 | 9.48 | 50 | 89.4 | 44.4 | 78.3 | 57.2 | 207.8 | 193.5 | 193.5 | NO
| NG | 103 | 111 | 31 | 17 | 110.9 | 23.1 | 50 | 89.4 | 44.4 | 61.8 | 72.6 | 209.5 | 205.1 | 205.1 | NO
| NG | 76 | 85 | 108 | 26 | 3.1 | 9.46 | 50 | 89.4 | 44.4 | 78.3 | 56.4 | 207.8 | 195.4 | 195.4 | NO
| NG | 111 | 104 | 31 | 17 | 110.9 | 22.62 | 50 | 89.4 | 44.4 | 62.4 | 72 | 209.5 | 205 | 205 | NO
| NG | 104 | 8 | 31 | 17 | 110.9 | 22.46 | 50 | 89.4 | 44.4 | 62.6 | 71.8 | 209.5 | 205 | 205 | NO
| NG | 8 | 9 | 31 | 17 | 110.9 | 21.19 | 50 | 89.4 | 44.4 | 64.1 | 70.4 | 209.5 | 204.7 | 204.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 45-004229
TR_B (available) | 61-010315
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 89.4
TR_B Baseline Loading% | 44.4
Total Scenarios Evaluated | 19
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 106
Switch Child Node | 130
Tie Node (TR_A side) | 130
Tie Node (TR_B side) | 26
Tie Line Distance (m) | 104.1
Load Transferred (kW) | 24.9
TR_A Loading After (%) | 59.8
TR_B Loading After (%) | 48.5
Minimum Voltage (V) | 214.6