## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 40 | 13 | 30 | 65 | 24.2 | 29.59 | 50 | 89.4 | 25 | 54.4 | 41.2 | 209.7 | 188.6 | 188.6 | NO
| NG | 40 | 106 | 133 | 8 | 54.2 | 40.17 | 50 | 89.4 | 25 | [5 empty] | NO | TR_B sim: not converged
| NG | 13 | 6 | 30 | 65 | 24.2 | 28.12 | 50 | 89.4 | 25 | 56.1 | 41.2 | 209.7 | 188.6 | 188.6 | NO
| NG | 106 | 130 | 133 | 8 | 54.2 | 24.9 | 50 | 89.4 | 25 | [5 empty] | NO | TR_B sim: not converged
| NG | 6 | 7 | 30 | 65 | 24.2 | 25.04 | 50 | 89.4 | 25 | 59.6 | 41.2 | 209.7 | 188.6 | 188.6 | NO
| NG | 130 | 129 | 133 | 8 | 54.2 | 24.9 | 50 | 89.4 | 25 | [5 empty] | NO | TR_B sim: not converged
| NG | 7 | 58 | 30 | 65 | 24.2 | 25.04 | 50 | 89.4 | 25 | 59.6 | 41.2 | 209.7 | 188.6 | 188.6 | NO
| NG | 129 | 88 | 133 | 8 | 54.2 | 24.76 | 50 | 89.4 | 25 | [5 empty] | NO | TR_B sim: not converged
| NG | 58 | 102 | 30 | 65 | 24.2 | 24.13 | 50 | 89.4 | 25 | 60.7 | 40.4 | 209.6 | 190.4 | 190.4 | NO
1 | OK | 88 | 50 | 53 | 8 | 113.5 | 14.63 | 50 | 89.4 | 25 | 71.7 | 27.1 | 213 | 218.9 | 213 | YES
| NG | 102 | 103 | 30 | 65 | 24.2 | 23.7 | 50 | 89.4 | 25 | 61 | 3030 | 209.5 | 213 | 209.5 | NO
2 | OK | 50 | 51 | 53 | 8 | 113.5 | 13.86 | 50 | 89.4 | 25 | 72.5 | 27.1 | 213 | 218.9 | 213 | YES
| NG | 103 | 111 | 30 | 65 | 24.2 | 23.1 | 50 | 89.4 | 25 | 61.8 | 39.7 | 209.5 | 192.1 | 192.1 | NO
3 | OK | 51 | 52 | 53 | 8 | 113.5 | 12.01 | 50 | 89.4 | 25 | 74.7 | 25 | 213 | 223.7 | 213 | YES
| NG | 111 | 104 | 30 | 65 | 24.2 | 22.62 | 50 | 89.4 | 25 | 62.4 | 39.7 | 209.5 | 192.1 | 192.1 | NO
4 | ** OPTIMAL ** | 52 | 33 | 53 | 8 | 113.5 | 11.76 | 50 | 89.4 | 25 | 75 | 25 | 213 | 223.7 | 213 | YES
| NG | 104 | 8 | 30 | 65 | 24.2 | 22.46 | 50 | 89.4 | 25 | 62.6 | 39.7 | 209.5 | 192.1 | 192.1 | NO
| NG | 33 | 34 | 37 | 8 | 156.3 | 10.26 | 50 | 89.4 | 25 | 76.7 | 41.1 | 212.6 | 166.2 | 166.2 | NO
| NG | 8 | 9 | 30 | 65 | 24.2 | 21.19 | 50 | 89.4 | 25 | 64.1 | 39.7 | 209.5 | 192.1 | 192.1 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 45-004229
TR_B (available) | 68-006158
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 89.4
TR_B Baseline Loading% | 25
Total Scenarios Evaluated | 19
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 52
Switch Child Node | 33
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 113.5
Load Transferred (kW) | 11.76
TR_A Loading After (%) | 75
TR_B Loading After (%) | 25
Minimum Voltage (V) | 213