## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 10 | 6 | 27 | 6 | 21.6 | 18.33 | 50 | 77.8 | 6.8 | [5 empty] | NO | TR_A sim: ไม่พบ load meters: SUBTYPECODE=1 (point) หลังจากกรอง XF
| NG | 6 | 7 | 27 | 6 | 21.6 | 18.33 | 50 | 77.8 | 6.8 | [5 empty] | NO | TR_A sim: ไม่พบ load meters: SUBTYPECODE=1 (point) หลังจากกรอง XF
| NG | 7 | 27 | 27 | 6 | 21.6 | 18.33 | 50 | 77.8 | 6.8 | 0 | 21.8 | 230.9 | 193 | 193 | NO
| NG | 27 | 8 | 8 | 6 | 71.9 | 17.8 | 50 | 77.8 | 6.8 | 2 | 21.2 | 230.3 | 196.2 | 196.2 | NO
| NG | 8 | 9 | 9 | 27 | 98.1 | 17.37 | 50 | 77.8 | 6.8 | 3.7 | 21 | 229.8 | 194.6 | 194.6 | NO
| NG | 9 | 23 | 23 | 6 | 144.7 | 1.88 | 50 | 77.8 | 6.8 | 69.2 | 8.1 | 192 | 227.8 | 192 | NO
| NG | 9 | 15 | 15 | 27 | 109.6 | 10.15 | 50 | 77.8 | 6.8 | 10.9 | 14.8 | 226.4 | 206.1 | 206.1 | NO
1 | ** OPTIMAL ** | 15 | 16 | 14 | 5 | 162.2 | 10.15 | 50 | 77.8 | 6.8 | 32.1 | 14.5 | 218.2 | 210.9 | 210.9 | YES
| NG | 16 | 19 | 19 | 27 | 209 | 2.82 | 50 | 77.8 | 6.8 | 64.2 | 8.8 | 196 | 222.1 | 196 | NO
| NG | 16 | 22 | 14 | 5 | 162.2 | 7.33 | 50 | 77.8 | 6.8 | 43.9 | 12.2 | 208.6 | 219.4 | 208.6 | NO
| NG | 22 | 5 | 14 | 5 | 162.2 | 7.33 | 50 | 77.8 | 6.8 | 43.9 | 12.2 | 208.6 | 219.4 | 208.6 | NO
| NG | 5 | 17 | 14 | 5 | 162.2 | 6.04 | 50 | 77.8 | 6.8 | 49.4 | 11.2 | 205.6 | 222 | 205.6 | NO
| NG | 17 | 18 | 14 | 5 | 162.2 | 5.95 | 50 | 77.8 | 6.8 | 49.8 | 11.2 | 205.4 | 222.1 | 205.4 | NO
| NG | 18 | 28 | 28 | 5 | 200.4 | 3.08 | 50 | 77.8 | 6.8 | 62.7 | 9 | 198.2 | 226 | 198.2 | NO
| NG | 18 | 13 | 14 | 5 | 162.2 | 0.4 | 50 | 77.8 | 6.8 | 75.7 | 7 | 189.6 | 229.7 | 189.6 | NO
| NG | 28 | 29 | 29 | 5 | 210.9 | 2.87 | 50 | 77.8 | 6.8 | 63.6 | 8.8 | 197.7 | 226.3 | 197.7 | NO
| NG | 29 | 35 | 35 | 5 | 222.5 | 1.64 | 50 | 77.8 | 6.8 | 69.5 | 7.9 | 194.3 | 227.9 | 194.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 45-007495
TR_B (available) | 60-014049
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 77.8
TR_B Baseline Loading% | 6.8
Total Scenarios Evaluated | 17
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 16
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 162.2
Load Transferred (kW) | 10.15
TR_A Loading After (%) | 32.1
TR_B Loading After (%) | 14.5
Minimum Voltage (V) | 210.9