## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 45 | 46 | 8 | 149 | 32.1 | 21.17 | 50 | 75.8 | 50.4 | 25.1 | 56.2 | 225.1 | 196.9 | 196.9 | NO
| NG | 46 | 47 | 8 | 149 | 32.1 | 21.17 | 50 | 75.8 | 50.4 | 26.2 | 56.1 | 225.1 | 197.4 | 197.4 | NO
| NG | 47 | 48 | 8 | 149 | 32.1 | 21.05 | 50 | 75.8 | 50.4 | 26.4 | 56.1 | 225 | 197.4 | 197.4 | NO
| NG | 48 | 21 | 8 | 149 | 32.1 | 18.1 | 50 | 75.8 | 50.4 | 33.2 | 56.1 | 225 | 197.4 | 197.4 | NO
| NG | 21 | 23 | 8 | 149 | 32.1 | 16.28 | 50 | 75.8 | 50.4 | 37.4 | 54.4 | 224.2 | 205.3 | 205.3 | NO
| NG | 23 | 60 | 8 | 149 | 32.1 | 15.27 | 50 | 75.8 | 50.4 | 39.7 | 54.4 | 224.2 | 205.3 | 205.3 | NO
| NG | 60 | 61 | 8 | 149 | 32.1 | 15.27 | 50 | 75.8 | 50.4 | 39.7 | 54.4 | 224.2 | 205.3 | 205.3 | NO
| NG | 61 | 20 | 8 | 149 | 32.1 | 15.27 | 50 | 75.8 | 50.4 | 39.7 | 54.4 | 224.2 | 205.3 | 205.3 | NO
| NG | 20 | 19 | 8 | 149 | 32.1 | 14.59 | 50 | 75.8 | 50.4 | 41.2 | 54.4 | 224.2 | 205.3 | 205.3 | NO
| NG | 19 | 15 | 8 | 149 | 32.1 | 12.91 | 50 | 75.8 | 50.4 | 45.1 | 54.4 | 224.2 | 205.3 | 205.3 | NO
| NG | 15 | 18 | 8 | 149 | 32.1 | 6.2 | 50 | 75.8 | 50.4 | 61 | 54.2 | 216.5 | 205.9 | 205.9 | NO
| NG | 18 | 59 | 8 | 149 | 32.1 | 5.74 | 50 | 75.8 | 50.4 | 62.2 | 54.2 | 215.6 | 205.9 | 205.9 | NO
| NG | 59 | 68 | 8 | 149 | 32.1 | 5.68 | 50 | 75.8 | 50.4 | 62.3 | 54.2 | 215.5 | 205.9 | 205.9 | NO
| NG | 68 | 14 | 8 | 149 | 32.1 | 5.45 | 50 | 75.8 | 50.4 | 62.8 | 54.2 | 215.5 | 205.9 | 205.9 | NO
| NG | 14 | 12 | 8 | 149 | 32.1 | 4.65 | 50 | 75.8 | 50.4 | 64.7 | 53.9 | 215.7 | 207 | 207 | NO
| NG | 12 | 13 | 8 | 149 | 32.1 | 4.41 | 50 | 75.8 | 50.4 | 65.3 | 53.9 | 215.2 | 207 | 207 | NO
| NG | 13 | 62 | 8 | 149 | 32.1 | 4.41 | 50 | 75.8 | 50.4 | 65.3 | 53.9 | 215.2 | 207 | 207 | NO
| NG | 62 | 63 | 8 | 149 | 32.1 | 4.41 | 50 | 75.8 | 50.4 | 65.3 | 53.9 | 215.2 | 207 | 207 | NO
| NG | 63 | 11 | 8 | 149 | 32.1 | 4.41 | 50 | 75.8 | 50.4 | 65.3 | 53.9 | 215.2 | 207 | 207 | NO
1 | OK | 11 | 6 | 8 | 149 | 32.1 | 1.52 | 50 | 75.8 | 50.4 | 72.1 | 51.6 | 215.7 | 212.1 | 212.1 | YES
2 | OK | 6 | 7 | 9 | 149 | 79.9 | 0.79 | 50 | 75.8 | 50.4 | 73.8 | 51.1 | 216 | 212.7 | 212.7 | YES
3 | OK | 6 | 8 | 8 | 149 | 32.1 | 0.73 | 50 | 75.8 | 50.4 | 74 | 51 | 216 | 212.7 | 212.7 | YES
4 | ** OPTIMAL ** | 7 | 9 | 9 | 149 | 79.9 | 0.42 | 50 | 75.8 | 50.4 | 74.8 | 50.8 | 216.1 | 213 | 213 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-008284
TR_B (available) | 30-001296
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 75.8
TR_B Baseline Loading% | 50.4
Total Scenarios Evaluated | 23
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 9
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 149
Tie Line Distance (m) | 79.9
Load Transferred (kW) | 0.42
TR_A Loading After (%) | 74.8
TR_B Loading After (%) | 50.8
Minimum Voltage (V) | 213