## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 45 | 26 | 66 | 96 | 9.9 | 10.91 | 50 | 75.8 | 24.6 | 50.6 | 29.8 | 217.4 | 210.6 | 210.6 | YES
2 | OK | 26 | 25 | 66 | 96 | 9.9 | 9.59 | 50 | 75.8 | 24.6 | 53.7 | 29.1 | 217.4 | 211.5 | 211.5 | YES
3 | OK | 25 | 27 | 66 | 96 | 9.9 | 8.91 | 50 | 75.8 | 24.6 | 54.9 | 28.8 | 217.1 | 211.5 | 211.5 | YES
4 | OK | 27 | 1 | 66 | 96 | 9.9 | 8.47 | 50 | 75.8 | 24.6 | 56.2 | 28.6 | 217.1 | 211.4 | 211.4 | YES
5 | OK | 1 | 0 | 66 | 96 | 9.9 | 7.01 | 50 | 75.8 | 24.6 | 59.6 | 27.9 | 217.1 | 211.6 | 211.6 | YES
6 | OK | 0 | 3 | 66 | 96 | 9.9 | 5.97 | 50 | 75.8 | 24.6 | 62 | 27.4 | 217.1 | 211.6 | 211.6 | YES
7 | OK | 3 | 2 | 66 | 96 | 9.9 | 5.27 | 50 | 75.8 | 24.6 | 63.6 | 27.1 | 216.9 | 211.6 | 211.6 | YES
8 | OK | 2 | 4 | 66 | 96 | 9.9 | 5.09 | 50 | 75.8 | 24.6 | 64 | 27 | 216.9 | 211.6 | 211.6 | YES
9 | OK | 4 | 5 | 66 | 96 | 9.9 | 4.17 | 50 | 75.8 | 24.6 | 66.1 | 26.6 | 216.6 | 211.7 | 211.7 | YES
10 | OK | 5 | 56 | 66 | 96 | 9.9 | 4.17 | 50 | 75.8 | 24.6 | 66.1 | 26.2 | 216.6 | 211.7 | 211.7 | YES
11 | OK | 56 | 55 | 66 | 96 | 9.9 | 3.03 | 50 | 75.8 | 24.6 | 68.8 | 26 | 216.6 | 211.7 | 211.7 | YES
12 | OK | 55 | 32 | 66 | 96 | 9.9 | 3.03 | 50 | 75.8 | 24.6 | 68.8 | 26 | 216.6 | 211.7 | 211.7 | YES
13 | OK | 32 | 30 | 66 | 96 | 9.9 | 2.01 | 50 | 75.8 | 24.6 | 71.1 | 25.6 | 216.2 | 211.7 | 211.7 | YES
14 | OK | 30 | 31 | 31 | 95 | 28.4 | 1.76 | 50 | 75.8 | 24.6 | 71.7 | 25.4 | 216.2 | 211.7 | 211.7 | YES
15 | ** OPTIMAL ** | 30 | 33 | 66 | 96 | 9.9 | 0.25 | 50 | 75.8 | 24.6 | 75.2 | 24.7 | 215.8 | 211.8 | 211.8 | YES
16 | OK | 31 | 38 | 38 | 95 | 96.8 | 0.73 | 50 | 75.8 | 24.6 | 74.1 | 24.9 | 216 | 211.8 | 211.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-008284
TR_B (available) | 58-014203
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 75.8
TR_B Baseline Loading% | 24.6
Total Scenarios Evaluated | 16
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 33
Tie Node (TR_A side) | 66
Tie Node (TR_B side) | 96
Tie Line Distance (m) | 9.9
Load Transferred (kW) | 0.25
TR_A Loading After (%) | 75.2
TR_B Loading After (%) | 24.7
Minimum Voltage (V) | 211.8