## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 45 | 26 | 58 | 18 | 1.1 | 10.91 | 50 | 75.8 | 41.3 | 50.6 | 49.9 | 217.4 | 211.7 | 211.7 | YES
2 | OK | 26 | 25 | 58 | 18 | 1.1 | 9.59 | 50 | 75.8 | 41.3 | 53.7 | 49.9 | 217.4 | 211.7 | 211.7 | YES
3 | OK | 25 | 27 | 58 | 18 | 1.1 | 8.91 | 50 | 75.8 | 41.3 | 54.9 | 48.5 | 217.1 | 213.7 | 213.7 | YES
4 | OK | 27 | 1 | 58 | 18 | 1.1 | 8.47 | 50 | 75.8 | 41.3 | 56.2 | 48.5 | 217.1 | 213.7 | 213.7 | YES
5 | OK | 1 | 0 | 58 | 18 | 1.1 | 7.01 | 50 | 75.8 | 41.3 | 59.6 | 48.5 | 217.1 | 213.7 | 213.7 | YES
6 | OK | 0 | 3 | 58 | 18 | 1.1 | 5.97 | 50 | 75.8 | 41.3 | 62 | 48.5 | 217.1 | 213.7 | 213.7 | YES
7 | OK | 3 | 2 | 58 | 18 | 1.1 | 5.27 | 50 | 75.8 | 41.3 | 63.6 | 47.4 | 216.9 | 215.3 | 215.3 | YES
8 | OK | 2 | 4 | 58 | 18 | 1.1 | 5.09 | 50 | 75.8 | 41.3 | 64 | 47.4 | 216.9 | 215.3 | 215.3 | YES
9 | OK | 4 | 5 | 58 | 18 | 1.1 | 4.17 | 50 | 75.8 | 41.3 | 66.1 | 47.1 | 216.6 | 215.7 | 215.7 | YES
10 | OK | 5 | 56 | 58 | 18 | 1.1 | 4.17 | 50 | 75.8 | 41.3 | 66.1 | 47.1 | 216.6 | 215.7 | 215.7 | YES
11 | OK | 56 | 55 | 58 | 18 | 1.1 | 3.03 | 50 | 75.8 | 41.3 | 68.8 | 47.1 | 216.6 | 215.7 | 215.7 | YES
12 | OK | 55 | 32 | 58 | 18 | 1.1 | 3.03 | 50 | 75.8 | 41.3 | 68.8 | 47.1 | 216.6 | 215.7 | 215.7 | YES
13 | OK | 32 | 30 | 58 | 18 | 1.1 | 2.01 | 50 | 75.8 | 41.3 | 71.1 | 46.2 | 216.2 | 216.7 | 216.2 | YES
14 | ** OPTIMAL ** | 30 | 31 | 58 | 18 | 1.1 | 1.76 | 50 | 75.8 | 41.3 | 71.7 | 45.6 | 216.2 | 217.4 | 216.2 | YES
15 | OK | 31 | 38 | 58 | 18 | 1.1 | 0.73 | 50 | 75.8 | 41.3 | 74.1 | 43.1 | 216 | 218.8 | 216 | YES
16 | OK | 38 | 43 | 58 | 18 | 1.1 | 0.28 | 50 | 75.8 | 41.3 | 75.1 | 42 | 215.8 | 218.7 | 215.8 | YES
17 | OK | 43 | 44 | 58 | 18 | 1.1 | 0.28 | 50 | 75.8 | 41.3 | 75.1 | 42 | 215.8 | 218.7 | 215.8 | YES
18 | OK | 44 | 39 | 58 | 18 | 1.1 | 0.28 | 50 | 75.8 | 41.3 | 75.1 | 42 | 215.8 | 218.7 | 215.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-008284
TR_B (available) | 60-004828
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 75.8
TR_B Baseline Loading% | 41.3
Total Scenarios Evaluated | 18
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 31
Tie Node (TR_A side) | 58
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 1.1
Load Transferred (kW) | 1.76
TR_A Loading After (%) | 71.7
TR_B Loading After (%) | 45.6
Minimum Voltage (V) | 216.2