## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 45 | 46 | 41 | 36 | 2.5 | 21.17 | 50 | 75.8 | 24.8 | 25.1 | 33 | 225.1 | 216.4 | 216.4 | YES
2 | OK | 46 | 47 | 41 | 36 | 2.5 | 21.17 | 50 | 75.8 | 24.8 | 26.2 | 32.9 | 225.1 | 216.8 | 216.8 | YES
3 | OK | 47 | 48 | 41 | 36 | 2.5 | 21.05 | 50 | 75.8 | 24.8 | 26.4 | 32.9 | 225 | 216.8 | 216.8 | YES
4 | OK | 48 | 21 | 41 | 36 | 2.5 | 18.1 | 50 | 75.8 | 24.8 | 33.2 | 32.9 | 225 | 216.8 | 216.8 | YES
5 | ** OPTIMAL ** | 21 | 23 | 41 | 36 | 2.5 | 16.28 | 50 | 75.8 | 24.8 | 37.4 | 30.6 | 224.2 | 221.5 | 221.5 | YES
6 | OK | 23 | 60 | 41 | 36 | 2.5 | 15.27 | 50 | 75.8 | 24.8 | 39.7 | 30.6 | 224.2 | 221.5 | 221.5 | YES
7 | OK | 60 | 61 | 41 | 36 | 2.5 | 15.27 | 50 | 75.8 | 24.8 | 39.7 | 30.6 | 224.2 | 221.5 | 221.5 | YES
8 | OK | 61 | 20 | 41 | 36 | 2.5 | 15.27 | 50 | 75.8 | 24.8 | 39.7 | 30.6 | 224.2 | 221.5 | 221.5 | YES
9 | OK | 20 | 19 | 41 | 36 | 2.5 | 14.59 | 50 | 75.8 | 24.8 | 41.2 | 30.6 | 224.2 | 221.5 | 221.5 | YES
10 | OK | 19 | 15 | 41 | 36 | 2.5 | 12.91 | 50 | 75.8 | 24.8 | 45.1 | 30.6 | 224.2 | 221.5 | 221.5 | YES
11 | OK | 15 | 18 | 41 | 36 | 2.5 | 6.2 | 50 | 75.8 | 24.8 | 61 | 30.3 | 216.5 | 221.8 | 216.5 | YES
12 | OK | 18 | 59 | 41 | 36 | 2.5 | 5.74 | 50 | 75.8 | 24.8 | 62.2 | 30.3 | 215.6 | 221.8 | 215.6 | YES
13 | OK | 59 | 68 | 41 | 36 | 2.5 | 5.68 | 50 | 75.8 | 24.8 | 62.3 | 30.3 | 215.5 | 221.8 | 215.5 | YES
14 | OK | 68 | 14 | 41 | 36 | 2.5 | 5.45 | 50 | 75.8 | 24.8 | 62.8 | 30.3 | 215.5 | 221.8 | 215.5 | YES
15 | OK | 14 | 12 | 41 | 36 | 2.5 | 4.65 | 50 | 75.8 | 24.8 | 64.7 | 29.8 | 215.7 | 222.3 | 215.7 | YES
16 | OK | 12 | 13 | 41 | 36 | 2.5 | 4.41 | 50 | 75.8 | 24.8 | 65.3 | 29.8 | 215.2 | 222.3 | 215.2 | YES
17 | OK | 13 | 62 | 41 | 36 | 2.5 | 4.41 | 50 | 75.8 | 24.8 | 65.3 | 29.8 | 215.2 | 222.3 | 215.2 | YES
18 | OK | 62 | 63 | 41 | 36 | 2.5 | 4.41 | 50 | 75.8 | 24.8 | 65.3 | 29.8 | 215.2 | 222.3 | 215.2 | YES
19 | OK | 63 | 11 | 41 | 36 | 2.5 | 4.41 | 50 | 75.8 | 24.8 | 65.3 | 29.8 | 215.2 | 222.3 | 215.2 | YES
20 | OK | 11 | 10 | 41 | 36 | 2.5 | 2.73 | 50 | 75.8 | 24.8 | 69.2 | 28 | 215.4 | 224.7 | 215.4 | YES
21 | OK | 11 | 6 | 9 | 34 | 110.6 | 1.52 | 50 | 75.8 | 24.8 | 72.1 | 26.5 | 215.7 | 226.1 | 215.7 | YES
22 | OK | 10 | 42 | 41 | 36 | 2.5 | 0.07 | 50 | 75.8 | 24.8 | 75.6 | 24.9 | 215.9 | 226 | 215.9 | YES
23 | OK | 6 | 7 | 9 | 34 | 110.6 | 0.79 | 50 | 75.8 | 24.8 | 73.8 | 25.7 | 216 | 226 | 216 | YES
24 | OK | 6 | 8 | 8 | 34 | 127.7 | 0.73 | 50 | 75.8 | 24.8 | 74 | 25.6 | 216 | 226 | 216 | YES
25 | OK | 7 | 9 | 9 | 34 | 110.6 | 0.42 | 50 | 75.8 | 24.8 | 74.8 | 25.3 | 216.1 | 226 | 216.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-008284
TR_B (available) | 60-015616
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 75.8
TR_B Baseline Loading% | 24.8
Total Scenarios Evaluated | 25
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 21
Switch Child Node | 23
Tie Node (TR_A side) | 41
Tie Node (TR_B side) | 36
Tie Line Distance (m) | 2.5
Load Transferred (kW) | 16.28
TR_A Loading After (%) | 37.4
TR_B Loading After (%) | 30.6
Minimum Voltage (V) | 221.5