## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 27 | 58 | 11 | 86.5 | 8.91 | 50 | 75.8 | 50.2 | 54.9 | 62.2 | 217.1 | 208.3 | 208.3 | NO
| NG | 27 | 1 | 58 | 11 | 86.5 | 8.47 | 50 | 75.8 | 50.2 | 56.2 | 62.2 | 217.1 | 208.3 | 208.3 | NO
| NG | 1 | 0 | 58 | 11 | 86.5 | 7.01 | 50 | 75.8 | 50.2 | 59.6 | 62.2 | 217.1 | 208.3 | 208.3 | NO
1 | OK | 21 | 22 | 24 | 12 | 137.1 | 1.82 | 50 | 75.8 | 50.2 | 71.6 | 57.6 | 216.1 | 213.8 | 213.8 | YES
| NG | 0 | 3 | 58 | 11 | 86.5 | 5.97 | 50 | 75.8 | 50.2 | 62 | 62.2 | 217.1 | 208.3 | 208.3 | NO
2 | OK | 22 | 24 | 24 | 12 | 137.1 | 1.82 | 50 | 75.8 | 50.2 | 71.6 | 57.6 | 216.1 | 213.8 | 213.8 | YES
3 | OK | 3 | 2 | 58 | 11 | 86.5 | 5.27 | 50 | 75.8 | 50.2 | 63.6 | 60.3 | 216.9 | 210.7 | 210.7 | YES
4 | OK | 24 | 54 | 54 | 12 | 138.4 | 0.04 | 50 | 75.8 | 50.2 | 71.6 | 50.4 | 216.1 | 217.8 | 216.1 | YES
5 | OK | 2 | 4 | 58 | 11 | 86.5 | 5.09 | 50 | 75.8 | 50.2 | 64 | 60.3 | 216.9 | 210.7 | 210.7 | YES
6 | ** OPTIMAL ** | 54 | 53 | 53 | 12 | 142.1 | 0.04 | 50 | 75.8 | 50.2 | 71.6 | 50.4 | 216.1 | 217.8 | 216.1 | YES
7 | OK | 4 | 5 | 58 | 11 | 86.5 | 4.17 | 50 | 75.8 | 50.2 | 66.1 | 59.7 | 216.6 | 211.4 | 211.4 | YES
8 | OK | 5 | 56 | 58 | 11 | 86.5 | 4.17 | 50 | 75.8 | 50.2 | 66.1 | 59.7 | 216.6 | 211.4 | 211.4 | YES
9 | OK | 56 | 55 | 58 | 11 | 86.5 | 3.03 | 50 | 75.8 | 50.2 | 68.8 | 59.7 | 216.6 | 211.4 | 211.4 | YES
10 | OK | 15 | 16 | 49 | 12 | 110.3 | 6.71 | 50 | 75.8 | 50.2 | 59.9 | 51.1 | 214.9 | 217.5 | 214.9 | YES
| NG | 15 | 18 | 51 | 7 | 36 | 6.2 | 50 | 75.8 | 50.2 | 61 | 70.1 | 216.5 | 200.2 | 200.2 | NO
11 | OK | 55 | 32 | 58 | 11 | 86.5 | 3.03 | 50 | 75.8 | 50.2 | 68.8 | 59.7 | 216.6 | 211.4 | 211.4 | YES
12 | OK | 16 | 17 | 49 | 12 | 110.3 | 5.66 | 50 | 75.8 | 50.2 | 62.3 | 51.1 | 215.3 | 217.5 | 215.3 | YES
13 | OK | 16 | 36 | 28 | 22 | 136.7 | 1.05 | 50 | 75.8 | 50.2 | 73.4 | 50.2 | 215.3 | 217.8 | 215.3 | YES
| NG | 18 | 59 | 51 | 7 | 36 | 5.74 | 50 | 75.8 | 50.2 | 62.2 | 70.1 | 215.6 | 200.2 | 200.2 | NO
14 | OK | 32 | 30 | 58 | 11 | 86.5 | 2.01 | 50 | 75.8 | 50.2 | 71.1 | 58.3 | 216.2 | 213 | 213 | YES
15 | OK | 17 | 34 | 49 | 12 | 110.3 | 5.43 | 50 | 75.8 | 50.2 | 62.9 | 50.2 | 214.8 | 217.8 | 214.8 | YES
16 | OK | 36 | 67 | 28 | 22 | 136.7 | 0.06 | 50 | 75.8 | 50.2 | 75.7 | 50.2 | 215.6 | 217.8 | 215.6 | YES
| NG | 59 | 68 | 51 | 7 | 36 | 5.68 | 50 | 75.8 | 50.2 | 62.3 | 70.1 | 215.5 | 200.2 | 200.2 | NO
17 | OK | 30 | 31 | 58 | 11 | 86.5 | 1.76 | 50 | 75.8 | 50.2 | 71.7 | 57.3 | 216.2 | 214.1 | 214.1 | YES
18 | OK | 34 | 35 | 49 | 12 | 110.3 | 4.46 | 50 | 75.8 | 50.2 | 65.1 | 50.2 | 215.1 | 217.8 | 215.1 | YES
| NG | 68 | 14 | 51 | 7 | 36 | 5.45 | 50 | 75.8 | 50.2 | 62.8 | 70.1 | 215.5 | 200.2 | 200.2 | NO
19 | OK | 31 | 38 | 58 | 11 | 86.5 | 0.73 | 50 | 75.8 | 50.2 | 74.1 | 53.1 | 216 | 217.2 | 216 | YES
20 | OK | 35 | 37 | 49 | 12 | 110.3 | 3.01 | 50 | 75.8 | 50.2 | 68.5 | 50.2 | 215.3 | 217.8 | 215.3 | YES
| NG | 14 | 12 | 51 | 7 | 36 | 4.65 | 50 | 75.8 | 50.2 | 64.7 | 68.3 | 215.7 | 201.9 | 201.9 | NO
21 | OK | 38 | 43 | 58 | 11 | 86.5 | 0.28 | 50 | 75.8 | 50.2 | 75.1 | 51.3 | 215.8 | 217.6 | 215.8 | YES
| NG | 12 | 13 | 51 | 7 | 36 | 4.41 | 50 | 75.8 | 50.2 | 65.3 | 68.3 | 215.2 | 201.9 | 201.9 | NO
22 | OK | 43 | 44 | 58 | 11 | 86.5 | 0.28 | 50 | 75.8 | 50.2 | 75.1 | 51.3 | 215.8 | 217.6 | 215.8 | YES
| NG | 13 | 62 | 51 | 7 | 36 | 4.41 | 50 | 75.8 | 50.2 | 65.3 | 68.3 | 215.2 | 201.9 | 201.9 | NO
23 | OK | 44 | 39 | 58 | 11 | 86.5 | 0.28 | 50 | 75.8 | 50.2 | 75.1 | 51.3 | 215.8 | 217.6 | 215.8 | YES
| NG | 62 | 63 | 51 | 7 | 36 | 4.41 | 50 | 75.8 | 50.2 | 65.3 | 68.3 | 215.2 | 201.9 | 201.9 | NO
| NG | 63 | 11 | 51 | 7 | 36 | 4.41 | 50 | 75.8 | 50.2 | 65.3 | 68.3 | 215.2 | 201.9 | 201.9 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 45-008284
TR_B (available) | 60-022573
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 75.8
TR_B Baseline Loading% | 50.2
Total Scenarios Evaluated | 36
Feasible Scenarios | 23
--- Optimal Solution ---
Switch Parent Node | 54
Switch Child Node | 53
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 142.1
Load Transferred (kW) | 0.04
TR_A Loading After (%) | 71.6
TR_B Loading After (%) | 50.4
Minimum Voltage (V) | 216.1