## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 28 | 0 | 24 | 63.6 | 19.12 | 50 | 94.1 | 21.3 | 10.5 | 36.2 | 227.9 | 174.5 | 174.5 | NO
| NG | 28 | 29 | 0 | 24 | 63.6 | 19.12 | 50 | 94.1 | 21.3 | 18 | 36.2 | 226.5 | 174.5 | 174.5 | NO
| NG | 29 | 42 | 0 | 24 | 63.6 | 19.12 | 50 | 94.1 | 21.3 | 18 | 36.2 | 226.5 | 174.5 | 174.5 | NO
| NG | 42 | 54 | 0 | 24 | 63.6 | 18.56 | 50 | 94.1 | 21.3 | 20.2 | 36.1 | 226.5 | 174.7 | 174.7 | NO
| NG | 54 | 17 | 0 | 24 | 63.6 | 18.56 | 50 | 94.1 | 21.3 | 20.2 | 36.1 | 226.5 | 174.7 | 174.7 | NO
| NG | 17 | 16 | 0 | 24 | 63.6 | 17.04 | 50 | 94.1 | 21.3 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 21.3% (degenerate)
| NG | 16 | 50 | 0 | 24 | 63.6 | 15.14 | 50 | 94.1 | 21.3 | 33.2 | 23.1 | 225.6 | 6.9 | 6.9 | NO
| NG | 50 | 49 | 0 | 24 | 63.6 | 15.14 | 50 | 94.1 | 21.3 | 33.2 | 449.9 | 225.6 | 6.9 | 6.9 | NO
| NG | 49 | 45 | 0 | 24 | 63.6 | 14.67 | 50 | 94.1 | 21.3 | 35.1 | 33.6 | 225.6 | 184.1 | 184.1 | NO
| NG | 45 | 44 | 0 | 24 | 63.6 | 14.41 | 50 | 94.1 | 21.3 | 36 | 33.1 | 225.4 | 185.7 | 185.7 | NO
| NG | 44 | 43 | 0 | 24 | 63.6 | 14 | 50 | 94.1 | 21.3 | 37.6 | 32.4 | 225.1 | 188.1 | 188.1 | NO
| NG | 43 | 41 | 0 | 24 | 63.6 | 12.61 | 50 | 94.1 | 21.3 | 43 | 30.1 | 224.1 | 195.7 | 195.7 | NO
| NG | 41 | 2 | 0 | 24 | 63.6 | 12.01 | 50 | 94.1 | 21.3 | 45.3 | 29.2 | 223.2 | 198.7 | 198.7 | NO
| NG | 2 | 1 | 0 | 24 | 63.6 | 11.2 | 50 | 94.1 | 21.3 | 48.5 | 28 | 221.8 | 202.7 | 202.7 | NO
| NG | 1 | 10 | 0 | 24 | 63.6 | 10.41 | 50 | 94.1 | 21.3 | 51.6 | 26.8 | 220.2 | 206.2 | 206.2 | NO
| NG | 10 | 9 | 0 | 24 | 63.6 | 10.38 | 50 | 94.1 | 21.3 | 51.7 | 26.8 | 220.1 | 206.3 | 206.3 | NO
| NG | 9 | 20 | 0 | 24 | 63.6 | 9.69 | 50 | 94.1 | 21.3 | 54.4 | 26.2 | 219.1 | 207.7 | 207.7 | NO
| NG | 20 | 8 | 0 | 24 | 63.6 | 5.89 | 50 | 94.1 | 21.3 | 69.7 | 26.2 | 213.4 | 207.7 | 207.7 | NO
1 | ** OPTIMAL ** | 8 | 7 | 0 | 24 | 63.6 | 4.87 | 50 | 94.1 | 21.3 | 73.7 | 24.8 | 213.9 | 210.2 | 210.2 | YES
2 | OK | 7 | 22 | 0 | 24 | 63.6 | 4.87 | 50 | 94.1 | 21.3 | 73.7 | 24.8 | 213.9 | 210.2 | 210.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-009294
TR_B (available) | 63-004021
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 94.1
TR_B Baseline Loading% | 21.3
Total Scenarios Evaluated | 20
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 7
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 24
Tie Line Distance (m) | 63.6
Load Transferred (kW) | 4.87
TR_A Loading After (%) | 73.7
TR_B Loading After (%) | 24.8
Minimum Voltage (V) | 210.2