## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 12 | 70 | 37 | 74.2 | 6.64 | 50 | 85.1 | 22.8 | 61.8 | 43.3 | 218.3 | 210.2 | 210.2 | YES
2 | ** OPTIMAL ** | 12 | 11 | 70 | 37 | 74.2 | 3.05 | 50 | 85.1 | 22.8 | 73.3 | 34.9 | 216.7 | 217.3 | 216.7 | YES
3 | OK | 11 | 13 | 70 | 37 | 74.2 | 2.86 | 50 | 85.1 | 22.8 | 74 | 34.1 | 216.6 | 217.8 | 216.6 | YES
4 | OK | 13 | 43 | 70 | 37 | 74.2 | 2.03 | 50 | 85.1 | 22.8 | 77.2 | 30.8 | 216 | 219.9 | 216 | YES
5 | OK | 43 | 54 | 70 | 37 | 74.2 | 2.03 | 50 | 85.1 | 22.8 | 77.2 | 30.8 | 216 | 219.9 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-009753
TR_B (available) | 30-005495
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.1
TR_B Baseline Loading% | 22.8
Total Scenarios Evaluated | 5
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 11
Tie Node (TR_A side) | 70
Tie Node (TR_B side) | 37
Tie Line Distance (m) | 74.2
Load Transferred (kW) | 3.05
TR_A Loading After (%) | 73.3
TR_B Loading After (%) | 34.9
Minimum Voltage (V) | 216.7