## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 25 | 23 | 23 | 2 | 71.8 | 9.72 | 50 | 88.8 | 25.3 | 66.3 | 48.6 | 212 | 212.7 | 212 | YES
2 | OK | 23 | 24 | 24 | 2 | 76.7 | 9.37 | 50 | 88.8 | 25.3 | 67.1 | 47.8 | 212 | 212.6 | 212 | YES
| NG | 19 | 15 | 15 | 6 | 28.6 | 27.3 | 50 | 88.8 | 25.3 | 24 | 93.2 | 223.4 | 197.3 | 197.3 | NO
3 | OK | 24 | 22 | 22 | 2 | 96.9 | 9.37 | 50 | 88.8 | 25.3 | 67.1 | 47.8 | 212 | 212.7 | 212 | YES
| NG | 15 | 16 | 16 | 6 | 40.2 | 24.91 | 50 | 88.8 | 25.3 | 29.5 | 87.6 | 222.1 | 197.1 | 197.1 | NO
4 | OK | 22 | 10 | 10 | 2 | 124.1 | 7.3 | 50 | 88.8 | 25.3 | 71.9 | 43 | 210.8 | 212.5 | 210.8 | YES
| NG | 16 | 2 | 2 | 6 | 50.1 | 24.37 | 50 | 88.8 | 25.3 | 30.8 | 86.1 | 222.1 | 198.4 | 198.4 | NO
| NG | 2 | 3 | 7 | 7 | 50.3 | 23.36 | 50 | 88.8 | 25.3 | 33.1 | 80.4 | 222.1 | 214.9 | 214.9 | NO
5 | OK | 3 | 4 | 7 | 7 | 50.3 | 22.37 | 50 | 88.8 | 25.3 | 35.4 | 78 | 222.1 | 216.3 | 216.3 | YES
6 | OK | 4 | 5 | 7 | 7 | 50.3 | 21.94 | 50 | 88.8 | 25.3 | 36.3 | 77 | 222 | 216.4 | 216.4 | YES
7 | OK | 5 | 6 | 7 | 7 | 50.3 | 17.58 | 50 | 88.8 | 25.3 | 46.5 | 66.6 | 222 | 216.2 | 216.2 | YES
8 | ** OPTIMAL ** | 6 | 7 | 7 | 7 | 50.3 | 13.37 | 50 | 88.8 | 25.3 | 56.6 | 56.8 | 218.3 | 216.7 | 216.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-011570
TR_B (available) | 57-007804
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 88.8
TR_B Baseline Loading% | 25.3
Total Scenarios Evaluated | 12
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 7
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 50.3
Load Transferred (kW) | 13.37
TR_A Loading After (%) | 56.6
TR_B Loading After (%) | 56.8
Minimum Voltage (V) | 216.7